|  |  |  | Job No: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Job Title: |  |  |  |
| DESIGN PROFORMA – Doc Reference XXXXXXXXXX |  |  |  |  |  |  |
| Date |  | Reviewed BY |  |  | Checked By |  |

This document is to be completed at the start of every design project by the Project Engineer.  The purpose is to identify the design parameters that will form the basis of the design going forward, along with identifying any risks that need to be managed.

Any project specifications issued by the client will supersede the COMPANY NAME standard information and be noted below.  It is the responsibility of the Project Engineer to review all the tender information and highlight any differences.  This review will help populate the Request For Information Schedule.  Once this completed this document shall be issued to the client for sign off/ comment.

| List of the Information provided at Tender Stage |  |
| --- | --- |
| Document | Comments |
| Drawings | Comments |

Following review of the above information, please populate the information on the next pages.

This document is set up for information only.  Please add or omit information as required.

|  | COMPANY NAME Standard | Any project specification that Supersedes |
| --- | --- | --- |
| Scope of Works – List/Delete as required | - Ventilation - Domestics Water Services - Drainage - Compressed Air - Chilled Water - Process Chilled Water - Hygiene Systems - LTHW - Specialist Gases - Sanitaryware - Natural Gas/ LPG - Incoming Water Services - Controls |  |

| Design Stage adopted | Stage 2 Stage 3 Stage 4 |  |
| --- | --- | --- |
| COMPANY NAME Deliverable Design Stage | Stage 2 Stage 3 Stage 4 Stage 5 |  |
| Design Responsibility for (COMPANY NAME) |  |  |
| Specific Contractor Design Elements |  |  |
| BREEAM/BRUKL/Thermal Modelling |  |  |
| Deliverables – AutoCAD, Revit (coordination only), BIM level 2 |  |  |
| Who is responsible for coordination? |  |  |
| Are there any 3rd party interfaces we need to connect to i.e. process contractor. |  |  |
| Risk to COMPANY NAME - (list out risks i.e. procurement/lead in/ interfaces/lack of information/ dependencies/site restrictions) |  |  |
| How are any Risks to be mitigated/Managed? |  |  |

| Design Considerations |  |  |
| --- | --- | --- |
| Design Margins to be used/ Future needs |  |  |
| External Design Conditions (dB/wB°C) |  |  |
| Internal Design Conditions (dB/wB°C) |  |  |
| External conditions for plant sizing? | Winter -10°C db 100% RH Summer 35°C db 40% RH |  |
| Infiltration Winter (based on CIBSE Guide A Table 4.2) | 1.0 ac/h Larger buildings - Area 1500m2 – 0.75ac/h 5000m2 – 0.55ac/h |  |
| Infiltration Summer | 0.5ac/h |  |
| U Values – External Walls | 0.35 W/m2k |  |
| Ground Floor | 0.25 W/m2k |  |
| Roof | 0.25 W/m2k |  |
| Windows | 2.20 W/m2k |  |
| Roof Lights | 2.20 W/m2k |  |
| White Walling | 0.20 W/m2k |  |
| Internal Gains | Production Area – 100W/m Office Area – 125W/m Comms – 200W/m |  |
| Occupancy |  |  |

| Ventilation |  |  |  |
| --- | --- | --- | --- |
| Filtration Levels Required |  |  |  |
| Full Fresh Air/Recirculation/Heat Recovery |  |  |  |
| Cooling Coil(S) Type | CHW/DX |  |  |
| Coil Temperatures |  |  |  |
| Glycol (food grade?) |  |  |  |
| Heating Coil(S) type | Electric/LTHW/Steam/DX |  |  |
| Humidity Control/Type |  |  |  |
| Min Air Change Rates/Volumes |  |  |  |
| High Cares Areas? |  |  |  |
| Pressure Regimes? |  |  |  |
| DSEAR/ATEX Requirements? |  |  |  |
| Ductwork Material |  |  |  |
| Specialist filtration i.e. Carbon Filter etc |  |  |  |
| Extract Exhaust Termination Points – any height restrictions i.e. 3m for LEV exhaust, DW172, High velocity Discharge |  |  |  |
| Intake and Exhaust points – through wall, roof, min separation from intake/exhausts |  |  |  |
| Any canopies to be provided by COMPANY NAME or others? What design/capture velocity/specific flow rate | Light Loading 0.25m/s Applies to steaming ovens, boiling pans, bains marie and stock-pot stoves. Medium Loading 0.35m/s Applies to deep fat fryers, bratt pans, solid and open top ranges, and griddles. Heavy Loading 0.50m/s Applies to steam (plume capture) chargrills, mesquite and specialist broiler units. |  |  |
| Ductwork weights and supports |  |  |  |
| Fire Compartmentation – Fire Rated Ductwork Required, Fire or Fire & Smoke Dampers? |  |  |  |
| Insulation |  |  |  |
| Design Parameters - Ductwork |  |  |  |
| Maximum Aspect ratio | 3:1 (4:1 to be used in extreme cases) |  |  |
| Office environment (NR35-40) |  |  |  |
| Final Run out (to terminal) | 3.0 - 3.5m/s |  |  |
| Branch Ductwork | 5.0 - 6.0m/s |  |  |
| Main Ductwork/Plantroom | 6.0 - 7.5m/s |  |  |
| Max Pressure Drop | <1.0Pa/m |  |  |
| Production environment |  |  |  |
| Final Run out (to terminal) | 3.5 - 4.5m/s |  |  |
| Branch Ductwork | 6.0 - 7.0m/s |  |  |
| Main Ductwork/Plantroom | 7.0 – 8.0m/s |  |  |
| Max Pressure Drop | <1.0Pa/m |  |  |
| Design to DW144 for access hatches or TR/19 | DW 144 – need to state specification |  | Check specification if applicable for TR/19 |
| Kitchen Extract i.e. Canopy Extract (from DW172 18.13) |  |  |  |
|  | Supply | Extract |  |
| Main Runs | 6-8 m/s | 6-9 m/s |  |
| Branch Runs | 4-6 m/s | 5-7 m/s |  |
| Spigots | 3-5 m/s | 5-7 m/s |  |
| High Velocity Discharge |  | 12-15m/s |  |
| Local Extract Ventilation – i.e. Nederman (if nothing provided by 3rd party) | Min Velocity 12 - 15m/s |  |  |

| Pipework |  |  |
| --- | --- | --- |
| Medium |  |  |
| Pipework Material list |  |  |
| Pipework Fittings/type |  |  |
| Pipework Max Pressure |  |  |
| Any hygiene hoses which require Cat 5 separation? |  |  |
| Hygiene temperatures/Blending Valves |  |  |
| Any high-pressure water systems >5Bar – suitable pipework type and fittings |  |  |
| Pipework Max Pressure |  |  |
| Any Steam and condensate? |  |  |
| Pipework weights and supports |  |  |
| Pipework Max Pressure |  |  |
| Drainage Pipework Material |  |  |
| What sanitaryware are we providing? Stainless Steel/VC? |  |  |
| Knee operated or PIR sinks (include in E for M) |  |  |
| Connection onto existing systems? |  |  |
| Design Parameters - Pipework |  |  |
| Domestic Water Storage Temps | 60°C (minimum) |  |
| Secondary Circulation Return Temps F&R | 60/55°C |  |
| LTHW Flow/Return | 80/60°C |  |
| CHW Flow/Return | 6/12°C |  |
| Chilled Water flow | 2°C |  |
| Blended Water Temp | 42°C |  |
| Flowrate for Hoses – indicate hot or cold | 0.25l/s |  |
| Operating temperatures |  |  |
| Open water services | Copper/Steel Pipe up to 28mm dia <1.0m/s |  |
|  | Copper/Steel Pipe over 28mm dia <1.5m/s |  |
| Closed loop (LTHW/CHW) | <300Pa/m or 1.5m/s |  |
| Steam | <25m/s |  |
| Water Sizing – Loading Units | Design to BS8558 |  |
| Any fixed water supplies for equipment? |  |  |
| Incoming Water Services |  |  |
| Metering/type? |  |  |

| Compressed Air |  |  |
| --- | --- | --- |
| Compressed air – Duty (duty/standby) |  |  |
| Operating pressure | 7Bar |  |
| Outlet Pressures | 6Bar |  |
| Air Quality | 1:2:1 (ISO 8573-1:2010) – non direct food contact |  |
| Pipework Material |  |  |
| Outlets | isolation valve and filter regulator? |  |
| Sizing – 8Bar and above | Pipe system Δp ≤ 0.1 bar The following values are recommended for the individual sections of the system: – Main line Δp ≤ 0.04 bar – Distribution line Δp ≤ 0.04 bar – Connection line Δp ≤ 0.03 bar |  |
| Sizing – Less than 8 bar | In pipe systems with lower maximum pressures ( e.g., 3 bar op ) a pressure loss of 0,1 bar is higher in relative terms than in an 8 bar op system. In this case, a different value is recommended for the system as a whole: – Pipe system Δp ≤ 1,5 % pmax |  |

| Gas |  |  |
| --- | --- | --- |
| Gas Type | Natural Gas |  |
| Incoming Pressure at meter | 21mbar |  |
| Max pressure loss | 1mbar |  |
| Pipework Material |  |  |
| Solenoid Valve/max pressure drop |  |  |
| Linked to fire alarm? |  |  |
| Additional meters? Pressure Loss |  |  |
| Serving equipment? – confirm flowrate and pressure |  |  |
| Booster required/details |  |  |

| Controls |  |  |
| --- | --- | --- |
| Type | Standalone/BMS |  |
| Language | Trend/RDM/other please state |  |
| EMS required | 1mbar |  |
| Metering/Type | Pulsed/modbus/bacnet etc |  |
| Head end required /Link to existing |  |  |
| Linked to fire alarm? |  |  |
| Any specific control requirements |  |  |

| For Internal Use Only – Do not Issue |  |  |
| --- | --- | --- |
|  |  | Risk Management Measures |
| Design Programme duration |  |  |
| Key Dates for issue - |  |  |
| Risk Items – Please List:- |  |  |