## PROJECT SUMMARY
MECHANICAL EQUIPMENT SCHEDULES SCHEDULE INDEX & STATUS / ISSUE CHECKLIST
IP 02-05-14 Version 1
| Project No: |  |  |  |  | Lead Engineer Initials:
| Project: |  |  |  |  | Schedule Checker Initials:
| Date: |  |  |  |  | Approver Initials:
NOTES - USING THIS WORKBOOK
1 | At Project Inception make a copy of this MASTER to your project file. Then fill in Project No & Project Details above - this field populates all schedules.
2 | Fill in Engineer / Checker / Approver Details - this field populates all schedules
3 | * Select YES from list below if Equipment required on the project - The Item is then shown highlighted on the index, for printing to PDF issue
4 | Next insert a unique Schedule Ref for those you are using - this is carried through to each schedule (i.e. KEY-SCH-M-50-0001)
5 | Populate the schedule tabs in the workbook as the design progresses - less work to do at the end!!
6 | The template schedules are not exhaustive - Your project may have equipment / plant not covered - add in tabs as required.
7 | Insert new rows as necessary on each schedule for the number of items required. Don't copy tabs.
8 | Date Complete, Checked & Approved cells below will auto complete, as these fields are filled in on individual schedules.
9 | Once the workbook is Stage complete it can be reviewed as a whole for technical checking / issue approval. NEVER issue the Excel File - ONLY PDF.
| SCHEDULE REF / DOC No: | REV | MECHANICAL EQUIPMENT | *EQUIP REQUIRED ? | ISSUE STATUS | COMPLETE | CHECKED | APPROVED | COMMENT
| Populate Here | Auto | Add New Schedules as Required | Yes / No | Select | Select | Auto | Auto | Populate Here
VENTILATION
| KEY-SH-M-50-XXX | 1 | AHU
| KEY-SH-M-50-XXX | 0 | Fans
| KEY-SH-M-50-XXX | 0 | HRU
| KEY-SH-M-50-XXX | 0 | Attenuator
| KEY-SH-M-50-XXX | 0 | Louvres
| KEY-SH-M-50-XXX | 0 | Fire Damper
| KEY-SH-M-50-XXX | 0 | Motorised Damper
| KEY-SH-M-50-XXX | 0 | Roof Terminal
| KEY-SH-M-50-XXX | 0 | Grilles
| KEY-SH-M-50-XXX | 0 | Air Filter
CHILLED/REFRIDGERANT
| KEY-SH-M-50-XXX | 0 | Chiller
| KEY-SH-M-50-XXX | 0 | Process Chiller
| KEY-SH-M-50-XXX | 0 | DX
| KEY-SH-M-50-XXX | 0 | VRF
WATER
| KEY-SH-M-50-XXX | 0 | Booster Set
| KEY-SH-M-50-XXX | 0 | Tank
| KEY-SH-M-50-XXX | 0 | CAT 5
| KEY-SH-M-50-XXX | 0 | Shower
| KEY-SH-M-50-XXX | 0 | Water Heater
| KEY-SH-M-50-XXX | 0 | Expansion Vessel
| KEY-SH-M-50-XXX | 0 | Electric Water Heater
| KEY-SH-M-50-XXX | 0 | Meters
HEATING
| KEY-SH-M-50-XXX | 0 | Pumps
| KEY-SH-M-50-XXX | 0 | Gas Booster
| KEY-SH-M-50-XXX | 0 | Press Unit
| KEY-SH-M-50-XXX | 0 | Electric Panel Heater
| KEY-SH-M-50-XXX | 0 | Heater Battery
COMPRESSED AIR
| KEY-SH-M-50-XXX | 0 | Compressed Air
ELECTRICAL
| KEY-SH-M-50-XXX | 0 | Electrical Requirements | NO

## AHU
|  |  | Project No. | 0
|  |  | Project | 0
|  |  | Schedule | Air Handling Unit 01
|  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  | Revision | 1
|  |  | Date | 0
REFERENCE |  |  |  | AHU1 |  | Comments
APPLICATION |  |  |  | Single Deck Supply Only |  | with recirculation.
LOCATION |  |  |  | Internal - Plant Deck
System Served |  |  |  | Main Production Area
MANUFACTURER
MODEL
AHU Components |  |  |  | Supply | Extract
Inlet Section | Mixing Box | Fresh Air |  | 15% - Motorised Inlet Damper |  | include actuators
|  | Temp oC db/wb |  | -5/5 winter, 32/23 summer
|  | Recirculation Air |  | 85% - Motorised Inlet Damper
|  | Temp oC db/RH |  | 12-14oC, 50-70% RH
Panel Filter |  | Grade | Grade | G4 | G4 | Magnehelic/ Pressure Switch
Bag Filter |  | Grade | Grade | F7 |  | Magnehelic/ Pressure Switch
Heat Recovery |  | Type | Grade
|  | min efficiency | Grade
|  | Summer Air on (supply/Return) - °C/RH | Grade
|  | Summer Air off (supply/Return) - °C/RH | Grade
|  | Winter Air Off (supply/Return) - °C/RH | Grade |  |  | advised by Manufacturer
|  | Winter Air Off (supply/Return) - °C/RH | Grade |  |  | advised by Manufacturer
|  | Reclaim (kW) Summer/Winter | Grade |  |  | advised by Manufacturer
Heater Battery | Type |  | kW
| Duty | kW | kW |  |  | Duties to be confirmed and validated by the manufacturer during selection
| Air temperature on/off | ºC | ºC | ??°C /15°C |  | on coil temp to be determined by manufacturer based on mixed conditions. Adjustable off coil dependant on room conditions. | if LTHW coil, use same format at CHW section
| Medium |  |  | Electric |  | Thyristor Control to be included
| Electrical supply | V/A | l/sec |  |  | Duties to be confirmed and validated by the manufacturer during selection
| Rated current (Run/Start) | A | ºC |  |  | Duties to be confirmed and validated by the manufacturer during selection
Fan Section | Duty volume | m³/s |  | 7.3 |  | Fixed Volume
| External static pressure | Pa | Pa | 350
| Electrical supply | V/ph/Hz | V/ph/Hz
| Rated current (Run/Start) | A | A |  |  | To be confirmed and validated by the manufacturer during selection
| Motor rating | kW | kW |  |  | To be confirmed and validated by the manufacturer during selection
| Fan Types |  |  | EC Fans
Access Section |  |  |  | Yes |  | manufacturer to confirm during selection
Bag Filter |  | Grade | Grade | H11 |  | due to recirculation air
Access Section |  |  |  | Yes |  | manufacturer to confirm during selection
Cooling Coil | Type |  | kW | Chilled Water
| Duty | kW | kW |  |  | Duties to be confirmed and validated (including any fan gains) by the manufacturer during selection.
| Air temperature on/off | ºC | ºC | ?? / 3°C |  | on coil temp to be determined by manufacturer based on mixed conditions. Adjustable off coil dependant on room conditions.
| Liquid Medium |  |  | CHW |  | 25% glycol (food grade)
| Liquid flowrate | l/sec | l/sec |  |  | Duties to be confirmed and validated by the manufacturer during selection
| Liquid Flow/Return Temp | ºC | ºC | 0/5
| Liquid pressure drop | kPa | kPa |  |  | Duties to be confirmed and validated by the manufacturer during selection
PLEASE NOTE THAT THE OFF COIL TEMPERATURE NOTED FOR COOLING ABOVE IS THE TEMPERATURE OF THE SUPPLY AIR LEAVING THE AHU. ANY INTERNAL GAINS SHOULD BE INCLUDED IN THE CHILLED WATER COIL DUTY (AS CALCULATED BY THE MANUFACTURER) TO ENSURE THE SUPPLY AIR CONDITIONS ARE MET.
Specific Fan Power |  | W/(l/s) | W/(l/s) |  |  | manufacturer to confirm during selection
Controls |  | Controls |  | AHU to be complete with integral controls |  | include fault/run/enable
|  | Modbus/BACnet |  | Connection/interface to be included |  | to allow remote adjustment of parameters
|  | Heater Battery |  | Thyristor control and High Temp Cut Off to be included
|  | Defrost |  | Defrost to be included as required |  | To be confirmed and validated by the manufacturer during selection
General Unit Dimension Overall
| Length | mm | mm | 7500 |  | max noted. Actual dims to be confirmed by the manufacturer during selection
| Width | mm | mm | 2500 |  | max noted. Actual dims to be confirmed by the manufacturer during selection
| Height | mm | mm | 2500 |  | max noted. Actual dims to be confirmed by the manufacturer during selection
| Weight | kg | kg |  |  | To be confirmed and validated by the manufacturer during selection
Additional |  | Trap Size | Grade |  |  | Manufacturer to include for correctly sized plastic trap
Notes:
1. Fans to be capable of 10% flow & 21% Resistance Additional duty above stated valves.
2. Provide inlet guard/mesh
3. AHU manufactured to EUROVENT performance certification & ISO14001 | [6 empty] | Check notes are relevant and add/delete as required.
4. Base frame to be included (minimum 150mm deep) to allow installation of cooling coil drainage trap
5. AHU thermal performance, air leakage rate and structural strength to be in accordance with CEN standard EN 1886. Leakage rate shall be L2 or better.
6. Configuration of the unit is indicative. Order of components/configuration to be advised by manufacturer.
7. Humidity of air uncontrolled.

## Fans
|  |  | Project No. | 0
|  |  | Project | 0
|  |  | Schedule | Supply & Extract Fans
|  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  | Revision | 0
|  |  | Date | 0
Reference No. | System Ref: | Location | Type | No. Off. | Total Flow | External Resistance | Model | Duct Connection (mm) | Dimensions (mm) |  |  | SFP | Electrical Details |  |  | Notes/Control Method
[5 empty] | (m3/s) | (Pa) |  |  | L | W | H | (w/l/s) | Ph/Hz/V | Input (W) | FLC (A)
EF01 | WC & Changing Extract | Ceiling Void | Inline | 1 | 0.448 | [10 empty] | Local on/off controller
EF02 | Washroom Extract | Roof Void | Inline | 1 | 0.833 | [10 empty] | Local on/off controller
EF03 | Office 2 | Roof Void | Inline | 1 | 0.06 | [10 empty] | Local on/off controller
EF04 | Canopy C Extract | Roof Void | Kitchen Extract Inline | 1 | 1.76 | [10 empty] | omitted
EF05 | Canopy C Extract | Roof Void | Kitchen Extract Inline | 1 | 1.76 | [10 empty] | Local on/off controller interlocked with motorised dampers on supply grilles
EF06 | Canopy C Extract | Roof Void | Kitchen Extract Inline | 1 | 1.76 | [10 empty] | Local on/off controller interlocked with motorised dampers on supply grilles
EF07 | Canopy C Extract | Roof Void | Kitchen Extract Inline | 1 | 0.88 | [10 empty] | Local on/off controller interlocked with motorised dampers on supply grilles
EF08 | Canopy B Extract | Roof Void | Kitchen Extract Inline | 1 | 0.527 | [10 empty] | Local on/off controller interlocked with motorised dampers on supply grilles
EF09 | Canopy A Extract | Roof Void | Kitchen Extract Inline | 1 | 1.07 | [10 empty] | Local on/off controller interlocked with motorised dampers on supply grilles
EF10 | Battery Extract | Roof Void | Through Wall ATEX Fan | 1 | 0.315 | [10 empty] | Operation linked to battery charge equipment & hydrogen sensor c/w adjustable run on timer & speed controller
EF11 | FF Server Room | Roof Void | Inline | 1 | 0.02 | [10 empty] | Local on/off controller
SF01 | Filling Supply | Roof Void | Inline | 1 | 0.35 | [10 empty] | Local on/off controller
SF02 | Packing Supply | Roof Void | Inline | 1 | 0.35 | [10 empty] | Local on/off controller
Notes:
1. Fans to be capable of additional margin 10% Flow & 20% Resistance.

## HRU
|  |  |  | Project No. | 0
|  |  |  | Project | 0
|  |  |  | Schedule | Heat Recovery Unit Schedule
|  |  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  |  | Revision | 0
|  |  |  | Date | 0
Reference No. | System Ref: | Type | Flow | External Resistance | Model | Filtration | NR Level | Heater Battery (LPHW/Elec) | SFP | Electrical Details |  |  | Notes
|  |  | (m3/s) | (Pa) |  |  |  |  | (w/l/s) | Ph/Hz/V | Input (W) | FLC (A)
Mezz Floor
HRU-01 | Mezz Level | HRU | 0.44 | 125 | [8 empty] | Local controllers required.
Notes:
1. Model of fans to be confirmed by the manufacturer at the time of quotation.
2. Select on low to medium speed to meet NR noise levels
3. Flowrates and pressure apply to both supply and extract.

## Attenuator
|  |  | Project No. | 0
|  |  | Project | 0
|  |  | Schedule | Attenuator Schedule
|  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  | Revision | 0
|  |  | Date | 0
Reference No. | System Ref: | Flow | External Resistance | Noise Criteria | Model/Type | Duct Size (mm) | Dimensions (mm) |  |  | Notes
|  | (m3/s) | (Pa) |  |  |  | L | W | H
ATT-01 | EF01 - Exhaust | 0.448 | <50 |  |  | 400Æ
ATT-02 | EF01 - Extract | 0.448 | <50 |  |  | 400Æ
ATT-03 | SF01 - FAI | 0.35 | <50 |  |  | 350Æ
ATT-04 | SF01 - Supply | 0.35 | <50 |  |  | 350Æ
ATT-05 | EF02 - Exhaust | 0.833 | <50 |  |  | 450Æ
ATT-06 | EF02 - Extract | 0.833 | <50 |  |  | 450Æ
ATT-07 | EF03 - Exhaust | 0.02 | <50 |  |  | 100Æ
ATT-08 | EF03 - Extract | 0.02 | <50 |  |  | 100Æ
ATT-09 | SF02 - FAI | 0.35 | <50 |  |  | 350Æ
ATT-10 | SF02 - Supply | 0.35 | <50 |  |  | 350Æ
ATT-11 | EF11 - Exhaust | 0.02 | <50 |  |  | 100Æ
ATT-12 | EF11 - Extract | 0.02 | <50 |  |  | 100Æ
Notes:

## Louvres
|  | Project No. |  | 0
|  | Project |  | 0
|  | Schedule |  | External Louvres
|  | Schedule No. |  | KEY-SH-M-50-XXX
|  | Revision |  | 0
|  | Date |  | 0
Reference No. | System | Flow (m3/s) | No. Off. | Louvre Type | Louvre Size (opening) | Bird Screen | Insect Screen | Motorised Damper | Pressure Loss (Pa) | Max Noise Level (dB) | Finish/Colour | Notes
EL1 | EF01 - WC & Changing Extract | 0.448 | 1 | Min. Class B | 850x850 | Y | Y |  | <20 | 35 | Standard finish, colour to be confirmed by Architect | c/w bird screen
EL2 | SF01 - Filling | 0.35 | 1 | Min. Class B | 750x750 | Y | Y |  | <20 | 35 | Standard finish, colour to be confirmed by Architect | c/w bird screen
EL3 | EF02 - Washroom Extract | 0.833 | 1 | Min. Class B | 1250x1000 | Y | Y |  | <20 | 35 | Standard finish, colour to be confirmed by Architect | c/w bird screen
EL4 | Fresh Air Makeup - Washroom | 0.42 | 1 | Min. Class B | 800x800 | Y | Y |  | <20 | 35 | Standard finish, colour to be confirmed by Architect | c/w bird screen
EL5 | Fresh Air Makeup - Washroom | 0.42 | 1 | Min. Class B | 800x800 | Y | Y |  | <20 | 35 | Standard finish, colour to be confirmed by Architect | c/w bird screen
EL6 | Battery Charge Makeup - Access Corridor | 0.16 | 1 | Min. Class B | 500x500 | Y | Y | Y | <20 | 35 | Standard finish, colour to be confirmed by Architect | c/w bird screen
EL7 | EF10 - Access Corridor | 0.32 | 1 | Min. Class B | 700x700 | Y | Y |  | <20 | 35 | Standard finish, colour to be confirmed by Architect | c/w bird screen
EL8 | Canopies Fresh Air Makeup - Access Corridor | 7.8 | 1 | Min. Class B | 4000x3000 | Y | Y |  | <20 | 35 | Standard finish, colour to be confirmed by Architect | c/w bird screen
EL9 | Battery Charge Makeup - Access Corridor | 0.16 | 1 | Min. Class B | 500x500 | Y | Y | Y | <20 | 35 | Standard finish, colour to be confirmed by Architect | c/w bird screen
EL10 | SF02 - Internet Sales | 0.35 | 1 | Min. Class B | 750x750 | Y | Y |  | <20 | 35 | Standard finish, colour to be confirmed by Architect | c/w bird screen
Notes:
Louvre sizes are based on min 50% free area. Manufacturer to confirm size at time of selection based on flowrate and max pressure loss.

## Fire Damper
|  |  | Project No. | 0
|  |  | Project | 0
|  |  | Schedule | Fire & Fire Smoke Dampers
|  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  | Revision | 0
|  |  | Date | 0
Reference No. | Location / System | Type | Fire Damper Size mm (w x h) | Wall / Ceiling Type | Compartment Fire Rating (mins) | Installation Method | Hole Size mm (w x h) | Notes
Ground Floor Fire Dampers
FD-0-01 | AHU-02 - G50 Fat Store | Smoke shield 501 | 400x400 | Internal Wall - Eurobond Firemaster Extra |  | DWFX-F | 500x500 | Local 230v power required (by others) control via smoke damper monitoring panel
FD-0-02 | AHU-02 - G50 Fat Store | Smoke shield 501 | 600x400 | Internal Wall - Eurobond Firemaster Extra |  | DWFX-F | 700x500 | Local 230v power required (by others) control via smoke damper monitoring panel
FD-0-03 | AHU-02 - G50 Fat Store | Smoke shield 501 | 400x400 | Internal Wall - Eurobond Firemaster Extra |  | DWFX-F | 500x500 | Local 230v power required (by others) control via smoke damper monitoring panel
FD-0-04 | AHU-02 - G50 Fat Store | Smoke shield 501 | 600x400 | Internal Wall - Eurobond Firemaster Extra |  | DWFX-F | 700x500 | Local 230v power required (by others) control via smoke damper monitoring panel
FD-0-05 | AHU-02 - G58 Link Corridor | Smoke shield 601 | 400dia | Internal Wall - Eurobond Firemaster Extra |  | DWFX-F | 550x550 | Local 230v power required (by others) control via smoke damper monitoring panel
FD-0-06 | AHU-02 - G58 Link Corridor | Smoke shield 601 | 400dia | Internal Wall - Eurobond Firemaster Extra |  | DWFX-F | 550x550 | Local 230v power required (by others) control via smoke damper monitoring panel
Ground Floor Fire Smoke Dampers
FSD-0-01 | AHU-02 - G32 Production Stairwell | Smoke shield 501 | 600x500 | Internal Wall - Eurobond Firemaster Extra |  | DWFX-F | 700x600 | Local 230v power required (by others) control via smoke damper monitoring panel
FSD-0-02 | AHU-02 - G32 Production Stairwell | Smoke shield 501 | 600x500 | Internal Wall - Eurobond Firemaster Extra |  | DWFX-F | 700x600 | Local 230v power required (by others) control via smoke damper monitoring panel
FSD-0-03 | AHU-02 - G32 Production Stairwell | Smoke shield 501 | 1000x600 | Internal Wall - Eurobond Firemaster Extra |  | DWFX-F | 1100x700 | Local 230v power required (by others) control via smoke damper monitoring panel
FSD-0-04 | AHU-02 - G32 Production Stairwell | Smoke shield 501 | 800x500 | Internal Wall - Eurobond Firemaster Extra |  | DWFX-F | 900x600 | Local 230v power required (by others) control via smoke damper monitoring panel
FSD-0-05 | AHU-02 - G32 Production Stairwell | Smoke shield 501 | 1000x600 | Internal Wall - Eurobond Firemaster Extra |  | DWFX-F | 1100x700 | Local 230v power required (by others) control via smoke damper monitoring panel
FSD-0-06 | AHU-02 - G32 Production Stairwell | Smoke shield 501 | 800x500 | Internal Wall - Eurobond Firemaster Extra |  | DWFX-F | 900x600 | Local 230v power required (by others) control via smoke damper monitoring panel
First Floor Fire Dampers
FD-1-03 | EF-1-06 - F10 Female WC | Thermshield FD | 400x400 | Internal Wall - Type 9 British Gypsum Wall Partition System A206067 |  | ThermShield Standard Installation | 500x500
FD-1-04 | AHU-03 - F24 Shop Store | Thermshield FDC | 125dia | Internal Wall - Type 9 British Gypsum Wall Partition System A206067 |  | ThermShield Standard Installation | 300x300
FD-1-05 | AHU-03 - F24 Shop Store | Thermshield FDC | 125dia | Internal Wall - Type 9 British Gypsum Wall Partition System A206067 |  | ThermShield Standard Installation | 300x300
FD-1-06 | AHU-03 - F24 Shop Store | Thermshield FDC | 125dia | Internal Wall - Type 9 British Gypsum Wall Partition System A206067 |  | ThermShield Standard Installation | 300x300
FD-1-07 | AHU-03 - F24 Shop Store | Thermshield FDC | 125dia | Internal Wall - Type 9 British Gypsum Wall Partition System A206067 |  | ThermShield Standard Installation | 300x300
FD-1-08 | AHU-03 - F37 Shop Office | Thermshield FDC | 200dia | Internal Wall - Type 9 British Gypsum Wall Partition System A206067 |  | ThermShield Standard Installation | 350x350
FD-1-09 | AHU-03 - F30 Acc WC | Thermshield FDC | 200dia | Internal Wall - Type 9 British Gypsum Wall Partition System A206067 |  | ThermShield Standard Installation | 350x350
FD-1-10 | AHU-03 - F30 Acc WC | Thermshield FDC | 150dia | Internal Wall - Type 9 British Gypsum Wall Partition System A206067 |  | ThermShield Standard Installation | 300x300
FD-1-11 | AHU-03 - F31 Servery | Thermshield FD | 400x200 | Internal Wall - Type 9 British Gypsum Wall Partition System A206067 |  | ThermShield Standard Installation | 500x300
First Floor Fire Smoke Dampers
FSD-1-01 | AHU-03 - F01 Link Bridge | Smoke shield 601 | 125dia | Internal Wall - Type 10 British Gypsum Wall Lining System B216027 |  | DWFX-F | 300x300 | Local 230v power required (by others) control via smoke damper monitoring panel
FSD-1-02 | AHU-03 - F01 Link Bridge | Smoke shield 601 | 125dia | Internal Wall - Type 10 British Gypsum Wall Lining System B216027 |  | DWFX-F | 300x300 | Local 230v power required (by others) control via smoke damper monitoring panel
FSD-1-03 | AHU-03 - F07B Shower Room | Smoke shield 601 | 125dia | Internal Wall - Type 11 British Gypsum Wall Partition System Q606052 |  | DWFX-F | 300x300 | Local 230v power required (by others) control via smoke damper monitoring panel
FSD-1-04 | AHU-03 - F07B Shower Room | Smoke shield 601 | 125dia | Internal Wall - Type 11 British Gypsum Wall Partition System Q606052 |  | DWFX-F | 300x300 | Local 230v power required (by others) control via smoke damper monitoring panel
FSD-1-05 | AHU-03 - F07B Shower Room | Smoke shield 601 | 100dia | Internal Wall - Type 11 British Gypsum Wall Partition System Q606052 |  | DWFX-F | 300x300 | Local 230v power required (by others) control via smoke damper monitoring panel
FSD-1-06 | AHU-03 - F12 Male WC | Smoke shield 601 | 200dia | Internal Wall - Type 11 British Gypsum Wall Partition System Q606052 |  | DWFX-F | 350x350 | Local 230v power required (by others) control via smoke damper monitoring panel
FSD-1-07 | AHU-03 - F12 Male WC | Smoke shield 601 | 100dia | Internal Wall - Type 11 British Gypsum Wall Partition System Q606052 |  | DWFX-F | 300x300 | Local 230v power required (by others) control via smoke damper monitoring panel
Fire & Smoke Damper Control Panel
FSDP
Notes:
Selections based on Action Air Fire Dampers
Builders work and fire stopping to be by others and approved by relevant parties i.e. Building Controls, Fire Stopping Contractor
Installation to comply fully with Manufacturer tested details. Any deviation from this to be agreed in writing with the Architect/building control officer/fire stopping contractor.

## Motorised Damper
|  |  | Project No. | 0
|  |  | Project | 0
|  |  | Schedule | Motorised Damper Schedule
|  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  | Revision | 0
|  |  | Date | 0
Reference No. | System Ref: | Duct Size | Damper Size | Model | Max PD (Pa) | Actuator |  | Electrical Details | Control - BMS/ Local/ AHU | Notes/Control links
Material/ Construction
|  | (mm) | (mm) |  |  |  |  | (V)
24V
24V
24V
24V
24V
24V
24V
24V
Notes:

## Roof Terminal
|  | Project No. |  | 0
|  | Project |  | 0
|  | Schedule |  | Roof Terminations
|  | Schedule No. |  | KEY-SH-M-50-XXX
|  | Revision |  | 0
|  | Date |  | 0
Reference No. | System / Location | Flow (m3/s) | No. Off. | Duct Size (mm) | Unit Size (mm) | Max PD (Pa) | Type | Notes
RT1 | EF04 | 0.448 | 1 | 500Æ | 500Æ |  | Roof Jet Exhaust Unit c/w Drain to Roof
RT2 | EF05 | 0.35 | 1 | 500Æ | 500Æ |  | Roof Jet Exhaust Unit c/w Drain to Roof
RT3 | EF06 | 0.833 | 1 | 500Æ | 500Æ |  | Roof Jet Exhaust Unit c/w Drain to Roof
RT4 | EF07 | 0.42 | 1 | 350Æ | 350Æ |  | Roof Jet Exhaust Unit c/w Drain to Roof
RT5 | EF08 | 0.42 | 1 | 300Æ | 300Æ |  | Roof Jet Exhaust Unit c/w Drain to Roof
RT6 | EF09 | 0.16 | 1 | 400Æ | 400Æ |  | Roof Jet Exhaust Unit c/w Drain to Roof
Notes:
1. Weathering, Builders work and Upstand by others. Terminal to be Free Issued to Builder for installation as required

## Grilles
|  |  |  | Project No. | 0
|  |  |  | Project | 0
|  |  |  | Schedule | Grilles & Diffuser Schedule
|  |  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  |  | Revision | 0
|  |  |  | Date | 0
Reference No. | System Ref: | No. Off. | Air Flow | Type | Dimensions | Spigot Size | Plenum | OBD | Motorised | PD | Throw | Max NR |  | Colour/Finish | Notes
Ceiling Type
|  |  | (l/s) |  | (mm) | (mm) |  |  |  | (Pa) | (m)
Ground Floor Extract
EG1 | Male WC | 1 | 24 | Valve | 150 | 100 | n/a | N |  |  |  | 35 |  | Standard RAL 9010
EG2 | Male WC | 1 | 24 | Valve | 150 | 100 | n/a | N |  |  |  | 35 |  | Standard RAL 9010
EG3 | Shower | 1 | 11 | Valve | 150 | 100 | n/a | N |  |  |  | 35 |  | Standard RAL 9010
EG4 | Shower | 1 | 11 | Valve | 150 | 100 | n/a | N |  |  |  | 35 |  | Standard RAL 9010
EG5 | Female WC | 1 | 30 | Valve | 150 | 100 | n/a | N |  |  |  | 35 |  | Standard RAL 9010
EG6 | Female WC | 1 | 30 | Valve | 150 | 100 | n/a | N |  |  |  | 35 |  | Standard RAL 9010
EG7 | Production Change | 1 | 80 | 4Way Diffuser Standard | 225x225 | 200 | Side Entry | N |  |  |  | 35 |  | Standard RAL 9010
EG8 | Lockers | 1 | 70 | 4Way Diffuser Standard | 225x225 | 200 | Side Entry | N |  |  |  | 35 |  | Standard RAL 9010
EG9 | Lockers | 1 | 70 | 4Way Diffuser Standard | 225x225 | 200 | Side Entry | N |  |  |  | 35 |  | Standard RAL 9010
EG10 | GMP Change | 1 | 100 | 4Way Diffuser Standard | 225x225 | 200 | Side Entry | N |  |  |  | 35 |  | Standard RAL 9010
EG11 | Washroom | 1 | 210 | 4Way Diffuser Stainless Steel | 400x400 | 300 | Side Entry | N |  |  |  | 35 |  | Stainless Steel
EG12 | Washroom | 1 | 210 | 4Way Diffuser Stainless Steel | 400x400 | 300 | Side Entry | N |  |  |  | 35 |  | Stainless Steel
EG13 | Washroom | 1 | 210 | 4Way Diffuser Stainless Steel | 400x400 | 300 | Side Entry | N |  |  |  | 35 |  | Stainless Steel
EG14 | Dirty | 1 | 210 | 4Way Diffuser Stainless Steel | 400x400 | 300 | Side Entry | N |  |  |  | 35 |  | Stainless Steel
EG15 | Office | 1 | 20 | 4Way Diffuser Standard | 150x150 | 100 | Side Entry | N |  |  |  | 35 |  | Standard RAL 9010
EG16 | Server | 1 | 20 | 4Way Diffuser Standard | 150x150 | 100 | Side Entry | N |  |  |  | 35 |  | Standard RAL 9010
First Floor Extract
EG17 | Server | 1 | 20 | 4Way Diffuser Standard | 150x150 | 100 | Side Entry | N |  |  |  | 35 |  | Standard RAL 9010
Ground Floor Supply
SG01 | Toppings | 1 | 1.3 | 4Way Diffuser Stainless Steel | 1000x1000 | n/a | n/a | N | Y |  |  | 35 |  | Stainless Steel
SG02 | Toppings | 1 | 1.3 | 4Way Diffuser Stainless Steel | 1000x1000 | n/a | n/a | N | Y |  |  | 35 |  | Stainless Steel
SG03 | Toppings | 1 | 1.3 | 4Way Diffuser Stainless Steel | 1000x1000 | n/a | n/a | N | Y |  |  | 35 |  | Stainless Steel
SG04 | Toppings | 1 | 1.3 | 4Way Diffuser Stainless Steel | 1000x1000 | n/a | n/a | N | Y |  |  | 35 |  | Stainless Steel
SG05 | Toppings | 1 | 1.3 | 4Way Diffuser Stainless Steel | 1000x1000 | n/a | n/a | N | Y |  |  | 35 |  | Stainless Steel
SG06 | Poppings | 1 | 1.3 | 4Way Diffuser Stainless Steel | 1000x1000 | n/a | n/a | N | Y |  |  | 35 |  | Stainless Steel
Notes:
1) All grille selections to be checked by supplier prior to procurement. Supplier to confirm throws, NR levels, PA drops, terminal velocities, and suitable space conditions under heating and cooling operation.
2) Throws/mounting heights are to be checked and confirmed by grille supplier prior to procurement/order placement.
3) Duct connection sizes to be checked and confirmed by grille supplier against coordinated drawings prior to procurement/order placement.
4) Ceiling types to be reviewed by grille provider prior to final procurement and manufacture.
5) Plenum connections to be reviewed against the coordinated drawings prior to procurement
6) All extract grilles to be either exhaust valves in WC areas and matched to the supply in other areas and where valves are not suitable. Valves should not be used for ventilation balancing. Duct mounted VCD's to be utilised for main balancing with final adjustments only on valves
7) Any grilles which cannot be selected against scheduled criteria are to be highlighted and queried prior to placing of order.
8) All Grille RAL Colours are to be confirmed by the architect prior to procurement/order placement.

## Air Filter
|  |  | Project No. | 0
|  |  | Project | 0
|  |  | Schedule | Air Filter
|  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  | Revision | 0
|  |  | Date | 0
Reference No. | System Ref | Type | Grade | Total Air Volume | Filter Size | Frame | Frame Size | Notes
|  |  |  | (m3/s) | (L x H x D mm) |  | (L x H x D mm)
FTR-01 | EL-01 | G4 Pleated Panel Filter | G4 | 2 | 1200 x 600 x 97 (2No. 594 x 594 x 97) | Front Withdrawal Frame | 1218 x 609 x 75 (2No. 609 x 609 x 75) | Filter grade G4 to EN779 and frame to include 4inch filter retaining clips & foam gasket to the filter sealing face
FTR-02 | EL-02 | G4 Pleated Panel Filter | G4 | 2 | 1200 x 600 x 97 (2No. 594 x 594 x 97) | Front Withdrawal Frame | 1218 x 609 x 75 (2No. 609 x 609 x 75) | Filter grade G4 to EN779 and frame to include 4inch filter retaining clips & foam gasket to the filter sealing face
FTR-03 | EL-03 | G4 Pleated Panel Filter | G4 | 2 | 1200 x 600 x 97 (2No. 594 x 594 x 97) | Front Withdrawal Frame | 1218 x 609 x 75 (2No. 609 x 609 x 75) | Filter grade G4 to EN779 and frame to include 4inch filter retaining clips & foam gasket to the filter sealing face
Notes:
1. To be supplied by Airclean Ltd or equal & approved.

## Chiller
|  |  | Project No. | 0
|  |  | Project | 0
|  |  | Schedule | Reverse Cycle Heat Pump Chiller
|  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  | Revision | 0
|  |  | Date | 0
REFERENCE |  |  |  | Chiller CH01 | Comments
APPLICATION |  |  |  | Reverse Cycle Heat Pump & Chiller
TYPE |  |  |  | Air Cooled
LOCATION |  |  |  | External
System Served |  |  |  | Samples Lab - AHU coil
MANUFACTURER
MODEL
Selection Data
External Design Conditions |  | ºC (dB/wB) | ºC | 35/30 (Summer)
|  | ºC (dB/wB) | ºC | -4/-4(Winter)
|  | min CoP |  | >3.5
Performance Data
Heating | Type |  | kW | Reversible Heat Pump Chiller
| Duty | kW | kW | 52 | min achieved at -4oC
| Liquid Medium |  |  | LTHW | 20% glycol
| Liquid flowrate | l/sec | l/sec |  | Duties to be confirmed and validated by the manufacturer during selection
| Liquid Flow Temp | ºC | ºC | 45 | adjustable from 30 to 45oC
| Liquid Return Temp | ºC | ºC | 40 | adjustable from 22 to 40oC
| Liquid pressure drop | kPa | kPa |  | Duties to be confirmed and validated by the manufacturer during selection
Cooling | Type |  | kW | Reversible Heat Pump Chiller
| Duty | kW | kW | 45 | min achieved at 35/30oC
| Liquid Medium |  |  | CHW | 20% glycol
| Liquid flowrate | l/sec | l/sec |  | Duties to be confirmed and validated by the manufacturer during selection
| Liquid Flow Temp | ºC | ºC | 6 | adjustable from 6 to 20oC
| Liquid Return Temp | ºC | ºC | 12 | adjustable from 12 to 27oC
| Liquid pressure drop | kPa | kPa |  | Duties to be confirmed and validated by the manufacturer during selection
| Fans |  |  | Variable speed. Number to suit unit | To be confirmed and validated by the manufacturer during selection
| Unit Electrical supply | V/ph/Hz | V/ph/Hz
| Rated current (Run/Start) | A | A |  | To be confirmed and validated by the manufacturer during selection
| Motor rating | kW | kW |  | To be confirmed and validated by the manufacturer during selection
| Compressor Types |  |  | Scroll (min 2No.compressors) | VSD
| Min System Volume | litre | A |  | Manufacturer to confirm min system volume required.
Refrigerant
Acoustic Information |  |  | 63Hz |  | To be confirmed and validated by the manufacturer during selection. Maximum sound pressure level at 5m from unit shall be 40dBA
125Hz
250Hz
500Hz
1kHz
2kHz
4kHz
8kHz
Controls |  | Controls |  | Unit to be complete with integral controls | See notes
|  | Modbus/BACnet |  | Connection/interface to be included | to allow remote adjustment of parameters
General Unit Dimension Overall
| Length | mm | mm
| Width | mm | mm
| Height | mm | mm
| Weight | kg | kg
Notes:
1. Refrigeration cycle to be reversible to operate in either cooling or heat pump mode
2. Re-set of evaporator & condenser entering and leaving water temperatures required via BMS 0-10v re-set signal
3. Heating & cooling medium = 20% glycol & water mix (Ethylene)
4. Chiller heat pump to operate in temperatures to -10°C
5. Circulation pump & strainer to be supplied integral with the chiller, system side pressure loss subject to confirmation
6. Flow switch for chill / heat pump enabling & shut off to be supplied with chiller and free issued for installation by mechanical installer.
7. Glycol / water side pressure safety valve to be integral to chiller heat pump
8. Winter anti-freeze pack and evaporator heater to be integral to chiller heat pump
9. Chiller heat pump to include communications module using MODBUS or BACNET.
10. BMS input signals to include; enable, disable and entering & leaving temperature re-set
11. Output signals to BMS to include defrost cycle and common fault notification.
12. Maximum sound pressure level at 5m from unit shall be 40dBA
13. Supply to include anti-vibration mountings and pipe flexible connections

## Process Chiller
|  |  | Project No. | 0
|  |  | Project | 0
|  |  | Schedule | Process Chiller
|  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  | Revision | 0
|  |  | Date | 0
REFERENCE |  |  |  | Process Chiller CH01 | Comments
APPLICATION |  |  |  | Process Chiller
TYPE |  |  |  | Air Cooled
LOCATION |  |  |  | External
System Served
MANUFACTURER
MODEL
Selection Data
External Design Conditions |  | ºC (dB/wB) | ºC | 35/30 (Summer)
|  | ºC (dB/wB) | ºC | -4/-4(Winter)
|  | min CoP |  | >3.0
Performance Data
Cooling | Type |  | kW | Process Chiller
| Duty | kW | kW | 45 | min achieved at 35/30oC
| Liquid Medium |  |  | CHW | 20% glycol (Ethylene)
| Liquid flowrate | l/sec | l/sec
| Liquid Flow Temp | ºC | ºC | -3
| Liquid Return Temp | ºC | ºC | 1
| Liquid pressure drop | kPa | kPa |  | Duties to be confirmed and validated by the manufacturer during selection
| Fans |  |  | Variable speed. Number to suit unit | To be confirmed and validated by the manufacturer during selection
| Unit Electrical supply | V/ph/Hz | V/ph/Hz
| Rated current (Run/Start) | A | A |  | To be confirmed and validated by the manufacturer during selection
| Motor rating | kW | kW |  | To be confirmed and validated by the manufacturer during selection
| Compressor Types |  |  | Scroll (min 2No.compressors) | VSD
| Min System Volume | litre | A |  | Manufacturer to confirm min system volume required.
| Integral Buffer |  |  | Yes | (if applicable)
| Integral Pump | min Ex Static at flowrate | A | 150 kPa | to be controlled by chiller
Refrigerant
Acoustic Information |  |  | 63Hz |  | To be confirmed and validated by the manufacturer during selection.
125Hz
250Hz
500Hz
1kHz
2kHz
4kHz
8kHz
Controls |  | Controls |  | Unit to be complete with integral controls | See notes
|  | Modbus/BACnet |  | Connection/interface to be included | to allow remote adjustment of parameters
General Unit Dimension Overall
| Length | mm | mm
| Width | mm | mm
| Height | mm | mm
| Weight | kg | kg
Notes:
1. Supply to include anti-vibration mountings and pipe flexible connections
2. Re-set of evaporator & condenser entering and leaving water temperatures required via BMS 0-10v re-set signal
3. Heating & cooling medium = 20% glycol & water mix (Ethylene)
4. Chiller heat pump to operate in temperatures to -10°C
5. Circulation pump & strainer to be supplied integral with the chiller, system side pressure loss subject to confirmation
6. Flow switch for chiller enabling & shut off to be supplied with chiller and free issued for installation by mechanical installer.
7. Glycol / water side pressure safety valve to be integral to chiller heat pump
8. Winter anti-freeze pack and evaporator heater to be integral to chiller heat pump
9. Chiller heat pump to include communications module using MODBUS or BACNET.
10. BMS input signals to include; enable, disable and entering & leaving temperature re-set
11. Output signals to BMS to include defrost cycle and common fault notification.

## DX
|  |  | Project No. | 0
|  |  | Project | 0
|  |  | Schedule | Air Conditioning (DX Split)
|  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  | Revision | 0
|  |  | Date | 0
REF | ROOM | MODEL | TYPE | SUPPLY FAN (Mi1) | COOLING CAPACITY | HEATING CAPACITY | ENTERING AIR |  | ELECTRICAL |  |  |  |  | DIMENSIONS | WEIGHT | Options and Accessories
|  |  |  | AIR FLOW RATE l/s | TOTAL kW | TOTAL kW | Winter oC | Summer oC | POWER SUPPLY |  |  | RUNNING CURRENT (A) Heating / Cooling | FUSE Rating (BS88) - HRC (A) | WxDxH | Net
Ground Floor Offices - Indoor Units
AC 01 | Office |  | Ceiling Cassette |  | 2.85 | 2 | 20 | 24 |  | 21.0 | 220V 1ph |  |  |  |  | Power fed from condenser
REF | System | Model | Type | COOLING CAPACITY Kw | HEATING CAPACITY kW | COP / EER (nominal) | REFRIG CHARGE | ELECTRICAL |  |  |  |  | DIMENSIONS | WEIGHT (kg) | Options and Accessories
[7 empty] | Factory Charge (kg) | VOLTAGE- PHASE | Starting CURRENT (A) | MIN CIRCUIT AMPS (MCA) | VOLTAGE- PHASE | RUNNING CURRENT (A) Heating / Cooling | (WxDxH) (mm)
Ground Floor Offices - Condensers
DX 01 | Office |  | External Condenser |  |  |  |  | 220V 1ph

## VRF
|  |  | Project No. | 0
|  |  | Project | 0
|  |  | Schedule | Air Conditioning (VRF)
|  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  | Revision | 0
|  |  | Date | 0
REF | ROOM | MODEL | TYPE | SUPPLY FAN (Mi1) | COOLING CAPACITY | HEATING CAPACITY | ENTERING AIR |  | ELECTRICAL |  |  |  |  | DIMENSIONS | WEIGHT | Options and Accessories
|  |  |  | AIR FLOW RATE l/s | TOTAL kW | TOTAL kW | Winter oC | Summer oC | POWER SUPPLY |  |  | RUNNING CURRENT (A) Heating / Cooling | FUSE Rating (BS88) - HRC (A) | WxDxH | Net
System 1
AC1-01 | EX A 181 - Meeting Room | PLFY-M32VEM-E | Ceiling Cassette |  | 2.6 | 2.08 | 20 | 24 | 220V 1ph | 21.0 | 220V 1ph |  |  |  | 24kg | Refnet?
AC1-02 | EX A 181 - Meeting Room | PLFY-M32VEM-E | Ceiling Cassette |  | 2.6 | 2.08 | 20 | 24 | 220V 1ph | [5 empty] | 24kg | Refnet?
AC1-03 | EX A 202 - Meeting Room | PLFY-P20VFM-E | 600 x 600 Ceiling Cassette |  | 2.2 | 1.76 | 20 | 24 | 220V 1ph | [5 empty] | 17kg
AC1-04 | EX A 202 - Meeting Room | PLFY-P20VFM-E | 600 x 600 Ceiling Cassette |  | 2.2 | 1.76 | 20 | 24 | 220V 1ph | [5 empty] | 17kg
AC1-05 | New Office | PKFY-P20VLM-E | Wall mounted Unit |  | 1.7 | 1.36 | 20 | 24 | 220V 1ph | [5 empty] | 17kg
AC1-06 | EX A 201 - Meeting Room | PKFY-P20VLM-E | Wall mounted Unit |  | 1.9 | 1.52 | 20 | 24 | 220V 1ph | [5 empty] | 17kg
AC1-17 | EX A 158 - Office | PLFY-P20VFM-E | 600 x 600 Ceiling Cassette |  | 2.25 | 1.8 | 20 | 24 | 220V 1ph | 21.0 | 220V 1ph |  |  |  | 17kg
AC1-18 | New Office | PLFY-P25VFM-E | 600 x 600 Ceiling Cassette |  | 2.25 | 1.8 | 20 | 24 | 220V 1ph | 21.0 | 220V 1ph |  |  |  | 17kg
REF | System | Model | Type | COOLING CAPACITY Kw | HEATING CAPACITY kW | COP / EER (nominal) | REFRIG CHARGE | ELECTRICAL |  |  |  |  | DIMENSIONS | WEIGHT (kg) | Options and Accessories
[7 empty] | Factory Charge (kg) | VOLTAGE- PHASE | Starting CURRENT (A) | MIN CIRCUIT AMPS (MCA) | VOLTAGE- PHASE | RUNNING CURRENT (A) Heating / Cooling | (WxDxH) (mm)
CU1 | System 1 | PURY-P450YNW-A2 | Heat Recovery Outdoor Unit (VRF) |  |  |  |  | 415V 3ph |  | 400V 3Nph | 415V 3ph |  |  |  | R32/R410A??
REF | System | MODEL | VOLTAGE- PHASE | FUSE Rating (BS88) – HRC (A) | RUNNING CURRENT (A) | DIMENSIONS (WxDxH mm) | WEIGHT (kg) Full
BC1 | System 1 | CMB-M1016V-JA1 | 230V 1ph
68kg
Cooling/heating loads are based on 125w/m2 (cooling) and 100w/m2 (heating)
System 2
AC2-01 | EX A 153 - Office | PLFY-P15VFM-E | 600 x 600 Ceiling Cassette |  |  |  | 20 | 24 | 220V 1ph | 21.0 | 220V 1ph |  |  |  | 17kg
AC2-02 | EX A 157 - Office | PLFY-P20VFM-E | 600 x 600 Ceiling Cassette |  |  |  | 20 | 24 | 220V 1ph | 21.0 | 220V 1ph |  |  |  | 17kg
AC2-03 | EX A 156 - Office | PLFY-P20VFM-E | 600 x 600 Ceiling Cassette |  |  |  | 20 | 24 | 220V 1ph | [5 empty] | 17kg
AC2-04 | EX A 152 - Office | PLFY-P15VFM-E | 600 x 600 Ceiling Cassette |  |  |  | 20 | 24 | 220V 1ph | [5 empty] | 17kg
AC2-05 | EX A 148 - Office | PLFY-P15VFM-E | 600 x 600 Ceiling Cassette |  |  |  | 20 | 24 | 220V 1ph | [5 empty] | 17kg
AC2-06 | EX A 151 - Office | PLFY-P15VFM-E | 600 x 600 Ceiling Cassette |  |  |  | 20 | 24 | 220V 1ph | [5 empty] | 17kg
AC2-07 | EX A 140 - Office | PLFY-P32VFM-E | 600 x 600 Ceiling Cassette |  |  |  | 20 | 24 | 220V 1ph | [5 empty] | 17kg
AC2-08 | EX A 139 - Office | PLFY-P20VFM-E | 600 x 600 Ceiling Cassette |  |  |  | 20 | 24 | 220V 1ph | [5 empty] | 17kg
AC2-24 | EX A 116 - Male Changing Room | PLFY-M32VEM-E | Ceiling Cassette |  |  |  | 20 | 24 | 220V 1ph | [5 empty] | 24kg
AC2-25 | EX A 101Female Changing Room | PLFY-M32VEM-E | Ceiling Cassette |  |  |  | 20 | 24 | 220V 1ph | [5 empty] | 24kg
[10 empty] | 21.0 | 220V 1ph
REF | System | Model | Type | COOLING CAPACITY Kw | HEATING CAPACITY kW | COP / EER (nominal) | REFRIG CHARGE | ELECTRICAL |  |  |  |  | DIMENSIONS | WEIGHT (kg) | Options and Accessories
[7 empty] | Factory Charge (kg) | VOLTAGE- PHASE | Starting CURRENT (A) | MIN CIRCUIT AMPS (MCA) | VOLTAGE- PHASE | RUNNING CURRENT (A) Heating / Cooling | (WxDxH) (mm)
CU1 | System 2 | PURY-P550YNW-A2 | Heat Recovery Outdoor Unit (VRF) |  |  |  |  | 415V 3ph |  | 400V 3Nph | 415V 3ph |  |  |  | Centralised controller required
REF | System | MODEL | VOLTAGE- PHASE | FUSE Rating (BS88) – HRC (A) | RUNNING CURRENT (A) | DIMENSIONS (WxDxH mm) | WEIGHT (kg) Full
BC1 | System 2 | CMB-M1016V-JA1 | 230V 1ph |  |  |  | 68kg
BC2 | System 2 | CMB-M108V-KB! | 230V 1ph |  |  |  | 48kg

## Booster Set
|  | Project No. |  | 0
|  | Project |  | 0
|  | Schedule |  | Booster Pump
|  | Schedule No. |  | KEY-SH-M-50-XXX
|  | Revision |  | 0
|  | Date |  | 0
Reference No. | System Ref: | Location | Duty (l/s @ bar) | Booster Set Type | Model Ref | Water Temp (°C) | WRAS Approved? | Duty/Standby or Duty/Assist | Weight (kg) | Sound Level db(A) | Associated Tank Size (litre) | Dimensions |  |  | Connections |  | Electrical Data |  |  | Notes
[12 empty] | L (mm) | W (mm) | H (mm) | Suction (mm) | Discharge (mm) | ph/hz/V | kW | FLC
BS1 | Domestic BCWS | Plantroom | 4.5 l/s @ 3 Bar | 3No. Stainless Steel Vertical Multi Stage Pumps | Lowara (Included in Ormandy Skid) | 10 | Yes | Duty/Duty/ Standby | [6 empty] | 67Ø | 67Ø | 3/50/400 | 4.5 |  | To include integral control panel with BMS interface.
BS2 | Process BCWS | Plantroom | 7.5 l/s @ 5 Bar | 3No. Stainless Steel Vertical Multi Stage Pumps | Lowara (Included in Ormandy Skid) | 10 | [8 empty] | 108Ø | 108Ø | 3/50/400 | 15 |  | To include integral control panel with BMS interface.
BS3 | Ingredients Room Process Cold Water | Plantroom | 7.5 l/s @ 5 Bar | 2No. Stainless Steel Vertical Multi Stage Pumps | Lowara (Included in Ormandy Skid) | 10 | [8 empty] | 108Ø | 108Ø | 3/50/400 | 15 |  | To include integral control panel with BMS interface.
BS4 | Ingredients Room Process Hot Water | Plantroom | 7.0 l/s @ 5 Bar | 2No. Stainless Steel Vertical Multi Stage Pumps | Lowara (Included in Ormandy Skid) | 65 | [8 empty] | 108Ø | 108Ø | 3/50/400 | 15 |  | To include integral control panel with BMS interface.
BS5 | Ingredients Room Chilled Water | Plantroom | 10.0 l/s @ 5 Bar | 2No. Stainless Steel Vertical Multi Stage Pumps | Lowara (Included in Ormandy Skid) | 2 | [8 empty] | 108Ø | 108Ø | 3/50/400 | 22 |  | To include integral control panel with BMS interface.
BS6 | HTHW Wash Down | Plantroom | 2.0 l/s @ 25 Bar | 2No. Stainless Steel Vertical Multi Stage Pumps | Lowara (Included in Ormandy Skid) | 65 | [8 empty] | 54Ø | 54Ø | 3/50/400 | 30 |  | To include integral control panel with BMS interface.
Notes:
1. Pumps to be selected with a minimum additional margin of 10% Flow & 21% Resistance.
2. Supplied by Grundfos Pumps or equal & approved.

## Tank
|  | Project No. |  | 0
|  | Project |  | 0
|  | Schedule |  | Water Storage Tank
|  | Schedule No. |  | KEY-SH-M-50-XXX
|  | Revision |  | 0
|  | Date |  | 0
Reference No. | System Ref: | Location | Capacity (L) Actual Required | Tank Type | No. Compartments | Connections |  | Dimensions |  |  | Overflow Pipe Size (mm) | Warning Pipe Size (mm) | Drain Size (mm) | Air Gap | Potable | Notes
[6 empty] | Inlet (mm) | Outlet (mm) | L (mm) | W (mm) | H (mm)
CWT1 | DOMESTIC BCWS | Plantroom | 1500 | GRP Sectional Externally Flanged Pre Insulated | 2 (Equal Split) | 2No. X 67mm | 2No. x 67mm | 2000*1 | 1000*1 | 1000 |  |  |  | AB |  | Tanks to include the following:- 2No x External Ladders 2No x Tank covers 2No x manhole access 2No x BMS Temp Detector pockets 2No x BMS H/Level Detector pockets 2No x BMS L/Level Detector pockets 2No x Water sampling valves 2No x Water Level indicators provide for each compartment Temperature warning alarm set to 18°C linked to BMS
HWT1 | INGREDIENTS ROOM PROCESS HOT WATER | Plantroom | 1500 | GRP Sectional or Stainless Steel TBC Temp 65C Externally Flanged Pre Insulated | 1 | 1No. X 67mm & 1No. X 108mm | 1No. x 108mm | 1000*1 | 1500*1 | 1500 |  |  |  | AG |  | Tanks to include the following:- 1No x External Ladders 1No x Tank covers 1No x manhole access 1No x BMS Temp Detector pockets 1No x BMS H/Level Detector pockets 1No x BMS L/Level Detector pockets 1No x Water sampling valves 1No x Water Level indicators provide for each compartment 1No x View Window Temperature warning alarm set to TBC°C linked to BMS
HWT2 | HIGH PRESSURE HOT WATER WASH DOWN | Plantroom | 1200 | GRP Sectional or Stainless Steel TBC Temp 65C Externally Flanged Pre Insulated | 1 | 1No. X 35mm & 1No. X 54mm | 1No. x 54mm | 1000*1 | 1000*1 | 1000 |  |  |  | AB |  | Tanks to include the following:- 1No x External Ladders 1No x Tank covers 1No x manhole access 1No x BMS Temp Detector pockets 1No x BMS H/Level Detector pockets 1No x BMS L/Level Detector pockets 1No x Water sampling valves 1No x Water Level indicators provide for each compartment 1No x View Window Temperature warning alarm set to TBC°C linked to BMS
Notes:
1. Manufacturer to confirm final tank dimensions

## CAT 5
|  |  | Project No. | 0
|  |  | Project | 0
|  |  | Schedule | CAT 5 Booster Pump
|  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  | Revision | 0
|  |  | Date | 0
Ref No. | System Ref: | Location | Duty (l/s @ bar) | Booster Set Type | Model Ref | Weight (kg) | Sound Level db(A) | Associated Tank Volume (Litre) | Dimensions |  |  | Connections |  | Electrical Data |  | Notes
[9 empty] | L (mm) | W (mm) | H (mm) | Suction (mm) | Discharge (mm) | ph/hz/V | FLC
CAT5-01 | CAT 5 | Plantroom | 1.2lt/s @ 3.0 bar | Run / standby pump with break tank | Boost -A - Break BTAB 3 -10 | [10 empty] | To include integral control panel with BMS interface.
Notes:
1. Pumps to be selected with a minimum additional margin of 10% Flow & 21% Resistance.
2. Supplied by Arrow Valves, Grundfos Pumps or equal & approved.

## Shower
|  |  |  | Project No. | 0
|  |  |  | Project | 0
|  |  |  | Schedule | Electric Shower Schedule
|  |  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  |  | Revision | 0
|  |  |  | Date | 0
Reference No. | System Ref. | Type | No. Off | Duty | Storage Capacity | Model | Max Temp | TMV 3 | Weight Full | Electrical Supply |  | Dimensions |  |  | Notes
|  |  |  | (kW) | (Litres) |  | (°C) | Required? | (kg) | ph/V/hz | Power (w) | H (mm) | L (mm) | W (mm)
SHW-01 | F05 Unisex Squat |  | 1 | 8.5 | NA |  | 40 | [7 empty] | Fed from CAT5 Supply, temperature control
SHW-02 | F22 Unisex Squat |  | 1 | 8.5 | NA |  | 40 | [7 empty] | Fed from CAT5 Supply, temperature control
Notes:
1. Showers to be complete with Hose, head and fixing rail

## Water Heater
|  |  |  | Project No. | 0
|  |  |  | Project | 0
|  |  |  | Schedule | Water Heater Schedule
|  |  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  |  | Revision | 0
|  |  |  | Date | 0
Reference No. | System Ref. | Type | No. Off | Storage Capacity | Coil Duty | Flow/Return Temp (C) | Model | Immersion Heaters No/kW | Construction | Max Recovery (L/h) | Max Gas Rate (m3/hr) | Flue size (mm) | Working/ Max Pressure (Bar) | Weight Full | Electrical Supply |  | Dimensions |  |  | Notes
|  |  |  | (Litres) | (kW) | [8 empty] | (kg) | ph/V/hazy | Power (w) | H (mm) | L (mm) | W (mm)
WH-01 | General Domestic Hot Water | LTHW Indirect + Electric Immersion | 1 | 800 | 80 | 60/55 |  | 1No. 3kW | Copper |  |  |  | 4/8 bar |  | 1/50/230 |  |  |  |  | Cylinder to come with controls for pasteurisation.
Notes:
1. Cylinder to be pre insulated to current Building Regulations.
2. Cylinder to be complete with Safety Valve, Pressure and Temperature Gauges, Anti Vac Valve, pockets for temperature and pressure sensors.

## Expansion Vessel
|  | Project No. |  | 0
|  | Project |  | 0
|  | Schedule |  | Expansion Vessel for Domestic Hot Water
|  | Schedule No. |  | KEY-SH-M-50-XXX
|  | Revision |  | 0
|  | Date |  | 0
Reference No. | System Ref: | System Volume | Pre Charge/Max | Model | Vessel Model Volume | Temperature (oC) | Weight (kg) | Glycol | Medium | Connection Size ("BSP) Inlet | Expansion Dimensions (Ø x H mm) | Notes
|  | (L) | (Bar Gauge)
EV-01 | Hot Water Cylinder | 11000 | 2.5/4.5 |  | 650 | 10/65 |  | n/a - Water Only | Domestic Water |  |  | Unit to be suitable for domestic water services - WRAS approved. Suitable for siting externally
Notes:
1. Manufacturer to check expansion volume/conditions and confirm requirements are satisfied.
2. Unit to be suitable for domestic hot water *WRAS Approved"

## Electric Water Heater
|  |  |  | Project No. | 0
|  |  |  | Project | 0
|  |  |  | Schedule | Electric Water Heater
|  |  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  |  | Revision | 0
|  |  |  | Date | 0
Reference No. | System Ref. | Type | No. Off | Duty | Storage Capacity | Model | Max Temp | TMV 3 | Weight Full | Electrical Supply |  | Dimensions |  |  | Notes
|  |  |  | (kW) | (Litres) |  | (°C) |  | (kg) | ph/V/hz | Power (w) | H (mm) | L (mm) | W (mm)
EWH-01 | PT13F - Sink | Unvented Undersink | 1 | 3 | 10 |  | 43 | Y |  | 1/230/50 | 3 |  |  |  | Temperature control, U2 Expansion pack inc. expansion vessel, relief valve & check valve
Notes:
1. To be mounted below sink

## Meters
|  | Project No. | 0
|  | Project | 0
|  | Schedule | Meters
|  | Schedule No. | KEY-SH-M-50-XXX
|  | Revision | 0
|  | Date | 0
Reference No. | Type & Description | System | Medium | Pipe Size | Max Flow Rate (l/s) | Min Flow Rate (l/s) | Pressure Loss | Meter Conn Size | Dimensions |  |  | Weight (kg) | Notes
[7 empty] | (kPa or mBar) | (mm) | L (mm) | W (mm) | H (mm)
Notes:
1. Turndown ratios be in line with manufactures requirements
2. Connection/meter/seals to be suitable for the medium served.

## Pumps
|  |  |  | Project No. | 0
|  |  |  | Project | 0
|  |  |  | Schedule | Pumps
|  |  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  |  | Revision | 0
|  |  |  | Date | 0
Reference No. | System Ref: | Flow | Resistance | Flow/Return Temp | Type/Model | Medium | Pipe Size | Dims (LxWxH) | Duty/ Standby? | WRAS Approved? | Glycol/ Type % | Pump Speed | Motor | Electrical Details |  |  | Notes
|  | (l/s) | (kPa) | (oC) | [7 empty] | (rpm) | (w) | Ph/Hz/V | Input (W) | FLC (A)
P1 | Secondary Circulation | 0.25 | 80 | 60/55 | Single Head -WRAS Approved |  | 35dia |  |  | Yes | N/A | [5 empty] | Pump with Inverter - suitable for domestic hot water
P2 | CT LTHW | 0.7 | 100 | 45/40 | Single Head Pump |  | 22dia |  |  | No | N/A | [5 empty] | Pump with inverter and ramp up/down on pressure
Notes:
1. Pumps to be capable of additional margin 10% Flow & 20% Resistance from what is noted above.
2. Pumps to be complete with flexible connections suitable for the medium.

## Gas Booster
|  |  |  | Project No. | 0
|  |  |  | Project | 0
|  |  |  | Schedule | Gas Booster
|  |  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  |  | Revision | 0
|  |  |  | Date | 0
Reference No. | System Ref: | Flowrate | Mains Pressure | Required Pressure | Type/Model | Max Inlet Pressure | Max Pressure Lift | Max Outlet Pressure | Weight | Noise | Electrical Details |  |  | Notes
|  | (m3/hr) | (mBar) | (mBar) |  | (mBar) | (mBar) | (mBar) | (kg) | (dBA) | Ph/Hz/V | Input (kW) | FLC (A)
GB1 | Natural gas to Steam Boilers | 365 | 21 | 65 | Utile Model 876A | [5 empty] | 3/50/400 | 3 |  | Boiler minimum operating pressure 62mBar, maximum 200mBar
GB2 | Natural gas to Steam Boilers | 365 | 21 | 65 | Utile Model 876A | [5 empty] | 3/50/400 | 3 |  | Boiler minimum operating pressure 62mBar, maximum 200mBar
Notes:

## Press Unit
Key Integrated Services Ltd Unit 2, Bollin Court Mill Lane Lymm Cheshire WA13 0SL TEL: 01925 759948 FAX: 01925 758400
|  | Project No. |  | 0
|  | Project |  | 0
|  | Schedule |  | Pressurisation Unit
|  | Schedule No. |  | KEY-SH-M-50-XXX
|  | Revision |  | 0
|  | Date |  | 0
Reference No. | System Ref: | System Volume | Pre Charge/Max | Press Unit Model | Vessel Model Volume (Litre) | Temperature (oC) | Weight (kg) | Glycol | Connection Size ("BSP) Inlet | Wall Unit dimensions (mm)(mm) | Expansion Vessel Diameter (Ø x H mm) | Electrical Details |  |  | Notes
|  | (L) | (Bar Gauge) | [8 empty] | Ph/Hz/V | Input (W) | FLC (A)
PU1 | Primary LTHW (Chiller) - Unit to be located externally | 1000 | 2.5/3.5 |  | 150 | 10/65 |  | n/a - Water Only | 1/2" | [5 empty] | Cold Feed by BCWS. System Static Head 10.0 m. Min fluid risk category 4 backflow preventer. Unit to be suitable for external position
Notes:
1. As manufactured by BOSS MIDI press fill
2. Suitable for external use
3. Manufacturer to check expansion volume/conditions and confirm requirements are satisfied.

## Electric Panel Heater
Key Integrated Services Ltd Unit 2, Bollin Court Mill Lane Lymm Cheshire WA13 0SL TEL: 01925 759948 FAX: 01925 758400
|  | Project No. |  |  |  | 0
|  | Project |  |  |  | 0
|  | Schedule |  |  |  | Electric Heater
|  | Schedule No. |  |  |  | KEY-SH-M-50-XXX
|  | Revision |  |  |  | 0
|  | Date |  |  |  | 0
Reference No. | System Ref: | Type | No. Off. | Area m2 | Duty @ 80w/m2 | Duty | Model | Electrical Details |  |  | Notes
[6 empty] | (Watts) |  | Ph/Hz/V | Input (W) | FLC (A)
Ground Floor Electric Heaters
EH-0-01 | Stairs | Panel Heater | 1 | 40 | 3200 | 3000 | PLXE |  |  |  | Inc 7 day programmable timer
First Floor Electric Heaters
EH-1-01 | F01 Link Bridge | Panel Heater | 1 | 46 | 3680 | 2000 | PLXE |  |  |  | Inc 7 day programmable timer
Notes:

## Heater Battery
Key Integrated Services Ltd Unit 2, Bollin Court Mill Lane Lymm Cheshire WA13 0SL TEL: 01925 759948 FAX: 01925 758400
[5 empty] | Project No. | 0
[5 empty] | Project | 0
[5 empty] | Schedule | Heater Batteries
[5 empty] | Schedule No. | KEY-SH-M-50-XXX
[5 empty] | Revision | 0
[5 empty] | Date | 0
Reference No. | Location Ref: | Type/Model | Area | w/m2 | Design Output | Actual Output | Air Flowrate | Fluid Flowrate | Water F&R Temps | Dimensions |  |  | Notes
[5 empty] | (W) | (W) | (l/s) | (l/s) | (°C) | L (mm) | H (mm) | D (mm)
Duct Mounted Heater Batteries
HB1 | F09 Male WCs | SPC Duct Mounted Coil | 21 | 60 | 1260 | 630 | 0.035 | 0.015072 | 80/70 | 150 | 150 | 75 | S and P Coils Code 12W1B6.2-4Tx150
HB2 | F09 Male WCs | SPC Duct Mounted Coil |  |  |  | 630 | 0.035 | 0.015072 | 80/70 | 150 | 150 | 75 | S and P Coils Code 12W1B6.2-4Tx150
HB3 | F10 Female WCs | SPC Duct Mounted Coil | 21 | 60 | 1260 | 630 | 0.035 | 0.015072 | 80/70 | 150 | 150 | 75 | S and P Coils Code 12W1B6.2-4Tx150
HB4 | F10 Female WCs | SPC Duct Mounted Coil |  |  |  | 630 | 0.035 | 0.015072 | 80/70 | 150 | 150 | 75 | S and P Coils Code 12W1B6.2-4Tx150
HB5 | F13 Female Lockers | SPC Duct Mounted Coil | 41 | 60 | 2460 | 3700 | 0.3 | 0.088517 | 80/70 | 315 | 315 | 75 | S and P Coils Code 12W1B8.1-8Tx315
HB6 | F14 Male Lockers | SPC Duct Mounted Coil | 80 | 60 | 4800 | 4930 | 0.4 | 0.11794 | 80/70 | 350 | 350 | 75 | S and P Coils Code 12W1B8.1-9Tx350
HB7 | F50 Female WC | SPC Duct Mounted Coil | 22 | 60 | 1320 | 1320 | 0.076 | 0.031579 | 80/70 | 200 | 200 | 75 | S and P Coils Code 12W1B12.1-5Tx200
HB8 | F51 Male WC | SPC Duct Mounted Coil | 22 | 60 | 1320 | 1320 | 0.076 | 0.031579 | 80/70 | 200 | 200 | 75 | S and P Coils Code 12W1B12.1-5Tx200
HB9 | F31 Servery | SPC Duct Mounted Coil |  |  | 12000 | 12000 | 0.45 |  | ELEC |  |  |  | Electric Heating Coil
HB10 | G40 QA Room | SPC Duct Mounted Coil |  |  | 7700 | 8000 | 0.3 |  | ELEC |  |  |  | Electric Heating Coil
HB11 | F53 QA Room | SPC Duct Mounted Coil |  |  | 7700 | 8000 | 0.3 |  | ELEC |  |  |  | Electric Heating Coil
Notes:

## Compressed Air
Key Integrated Services Ltd Unit 2, Bollin Court Mill Lane Lymm Cheshire WA13 0SL TEL: 01925 759948 FAX: 01925 758400
|  |  | Project No. | 0
|  |  | Project | 0
|  |  | Schedule | Compressed Air
|  |  | Schedule No. | KEY-SH-M-50-XXX
|  |  | Revision | 0
|  |  | Date | 0
REFERENCE |  |  |  | Compressed Air Plant | Comments
APPLICATION
LOCATION |  | internal/external
SYSTEM SERVED
COMPRESSED AIR QUALITY REQUIRED |  | (ISO8573-1:2010) |  | 1:2:1???? | non direct food contact???
TOTAL SYSTEM DUTY REQUIRED |  | CFM, m3/min
SYSTEM WORKING PRESSURE |  | BarG
MANUFACTURER
MODEL
Compressor | Capacity | CFM, m3/min
| Working Pressure | BarG
No.
| Duty or Duty/Standby | Duty or Duty/Standby |  |  | As applicable
| Type |  |  | Variable Speed Rotary screw etc?
| Oil Lubricated or Oil Free |  |  |  | Food Grade required?
| Size | (W xD x H mm) |  |  | advised by Manufacturer
| Weight | kg |  |  | advised by Manufacturer
| Motor Rating | (kW |  |  | advised by Manufacturer
| Electrical supply | V/ph/Hz | V/ph/Hz
| Rated current (Run/Start) | A | A
| Cooling Method | Air/Water |  |  | manufacturer to advise air flow rate for cooling purposes
Receiver | Type/Model | Type | Grade
| Capacity | Litres | Grade
| Orientation | Horizontal/Vertical
| Size | (Dia x H mm) |  |  | advised by Manufacturer
| Design Pressure | BarG |  |  | advised by Manufacturer
Dryer | Type |  | kW
| Working Pressure | BarG
| Capacity | CFM, m3/min
| Dew Point | ºC | ºC
| Electrical supply | V/ph/Hz | V/ph/Hz
| Rated current (Run/Start) | A | ºC
| Purge Air | CFM, m3/min
Filtration | Required Filtration - Pre Filters | AO |  |  | To be advised by Manufacturer to meet air quality
AA
| Required Filtration - Post Filters | AO
AA
Required Filtration - Carbon Tower
Condensate Management System |  | Type
| Electrical supply | V/ph/Hz | V/ph/Hz
| Rated current (Run/Start) | A | A
Controls |  | Controls |  | ??
|  | Modbus/BACnet |  | ??
Additional items/Sundry's |  |  |  |  | Manufacturer to include for correctly sized plastic trap
Notes:
1. Manufacturer to advise any elements that are required to meet the air quality standard
2. Manufacturer to advise of the air flow required to provide sufficient cooling to the units to comply with the Manufacturers recommendations
3. Manufacturer to provide data sheet of components to accompany the selection/quotation

## Electrical Requirements
|  | Project No. | 0 | [13 empty] | Key Integrated Services Ltd Unit 2, Bollin Court Mill Lane Lymm Cheshire WA13 9SX TEL: 01925 759948 FAX: 01925 758400
|  | Project | 0
|  | Schedule | Mechanical Power Requirements
|  | Schedule No. | KEY-SH-M-50-XXX
|  | Revision | 0
|  | Date | 0
Item Reference | Item Description | Qty | Location | Drawing No | Manufacturer | Model | ELECTRICAL DATA | [5 empty] | Data | Local Supply or BMS Panel | Priority | Linked to Fire Alarm (shut down) | Other
[7 empty] | Phase 1 or 3 | Voltage | SC (A) | FLC (A) | Fuse (A) | Load (kW)
Main Plant -External
CHW 01 | Heat Pump Chiller AHU 1 | 1 | External |  |  |  | 3 | 400 |  | 412 |  | 249.9 |  | local | 4 |  | In-rush - 650A
AHU 01 | Air Handling Unit | 1 | External |  |  |  | 3 | 400 |  | 5.5 |  | 3 |  | local | 3 |  | Per Pump - 3 Pump Included on the booster set
EF01 | LEV Fan | 1 | External | [13 empty] | inverter located adjacent to electrical panels.
EF02 A & B | LEV Fan | 2 | External | [13 empty] | inverter located adjacent to electrical panels.
- | Trace Heating | 2 | External |  |  |  | 1 | 230 |  | 16 |  |  |  | local
CU 1 | VRF Condenser | 1 | External |  |  |  | 3 | 400 |  |  | 32 |  |  | local | ASAP |  | Note there are 9no 1ph electrical supplies required to the FCU's/BC box in the office areas
Main Plant -Plantroom
AHU 01 | AHU 1 Supply Fan | 6 | Plantroom |  |  |  | 3 | 400 |  | 8.9 |  | 5.8 |  | local | 5 | Yes | 6 separate Isolators
| AHU 1 Extract Fan | 2 | Plantroom |  |  |  | 3 | 400 |  | 6.3 |  | 4.1 |  | local | 5 | yes | 2 separate Isolators
| AHU 1 Thermal Wheel | 1 | Plantroom |  |  |  | 1 | 230 |  | 2 |  | 0.55 |  | Internal |  |  | Internal Wired
AHU 02 | AHU 2 Supply Fan | 2 | Plantroom |  |  |  | 3 | 400 |  | 8.8 |  | 5.8 |  | local | 5 | Yes | 2 separate Isolators
| AHU 2 Extract Fan | 2 | Plantroom |  |  |  | 3 | 400 |  | 6.3 |  | 4.1 |  | local | 5 | yes | 2 separate Isolators
| AHU 2 Thermal Wheel | 1 | Plantroom |  |  |  | 1 | 230 |  | 2 |  | 0.55 |  | Internal | 5 |  | Internal Wired
- | AHU 2 Electric Heater Battery | 1 | Plantroom |  |  |  | 3 | 400 |  | 101 |  | 61.8 |  | local | 5 |  | Single stage Thyristor controlled
PU 01 | Press Unit 01 - AHU 01 | 1 | Plantroom |  |  |  | 1 | 230 |  | 2 | 6 |  |  | local | 6
PU 02 | Press Unit 02 - AHU 02 | 1 | Plantroom |  |  |  | 1 | 230 |  | 2 | 6 |  |  | local | 6
| Electric Water Heater 1 | 5 | Plantroom |  |  |  | 3 | 400 |  |  |  | 12 |  | local | 2 |  | 90 Amps per phase
HW 01 & 02 | Electric Water Heater 2 | 5 | Plantroom |  |  |  | 3 | 400 |  |  |  | 12 |  | local | 2 |  | 90 Amps per phase
P01 | Secondary Circulation Pump | 1 | Plantroom |  |  |  | 1 | 230 |  | 3 | 6 |  |  | local | 2 |  | secondary circulation pump
CAT 02 | CAT 5 Booster - Cold | 1 | Plantroom |  |  |  | 1 | 230 |  | 2.4 |  |  |  | local | 7
CAT 01 | CAT 5 Booster - Hot | 1 | Plantroom |  |  |  | 1 | 230 |  | 2.4 |  |  |  | local | 7
- | CAT 5 Booster - Hot - Immersion | 1 | Plantroom |  |  |  | 1 | 230 |  | 16 |  |  |  | local | 7 |  | Immersion mounted in tank
WS 01 | Water Softener | 1 | Plantroom |  |  |  | 1 | 230 |  |  | 6 |  |  | local | 3
EF-P-01 | Roof Extract Fan | 1 | Plantroom |  |  |  | 1 | 230 | 28 | 10 |  | 1.35 |  | local | ASAP |  | 28A SC
- | Trace Heating | 1 | Plantroom |  |  |  | 1 | 230 |  | 16 |  |  |  | local | ASAP
C1 & C2 | Compressed Air Compressors | 2 | Plantroom |  |  |  | 3 | 400 |  | 63 |  | 22 |  | local | 8
D1 | Desiccant Dryer | 1 | Plantroom |  |  |  | 1 | 230 |  |  | 20 |  |  | local | 8
MCCP | BMS Panel | 1 | Plantroom |  |  |  | 3 | 400 |  |  | 32 |  | Yes | local | 1 |  | Provide Data and FA interface to panel.
| Fire Dampers (FD-01-02 & 02), (FD-A2-01 & 02) | 5 | Plantroom Area |  |  |  | 1 | 230 |  | 5 |  |  |  | local | 3 | Yes | This also requires a FA interface
Engineers Store
R01 | RO Plant | 1 | F10 Engineers Store | KEY-01-DR-ME-90-101 | IWE | Promax 4 2000 | 3 | 400 |  |  | 20 | 4kW |  | local | 3 |  | 20 A Pre-Fusing on datasheet
Notes 1. Only the supplies for the Mechanical Equipment supplied and installed by Key IS are indicated on this schedule.. Client equipment/plant is not included. 2. The electrical contractor to provide power supplies were we have indicated local supplies. Where noted as BMS Panel, the power supply will be provided by the BMS Contractor. 3. Final Electrical connections to equipment to be by Electrical Contractor for continuity of Testing/Commissioning. 4. All Primary and Secondary containment to Mechanical equipment to be provided by the Electrical Contractor.
#REF!
0