## Watt Losses
Document Reference: 02-05-19-14 ¦ Version 1.0 ¦ This document is uncontrolled when printed. Refer to SharePoint for the latest version.
Calculation of Power Losses of Components Within Enclosure
Project No: |  |  | Client/Order No: |  | Calculation No:
Project: |  |  |  |  | Issue:
Date:
| Item Number | Device ID | Part Number | Item Description | Power Losses Each
|  |  |  | Total: | 0
| Calculated By: |  |  | Signed:
| Approved By: |  |  | Signed:

## Calc Sheet
Document Reference: 02-05-19-14 ¦ Version 1.0 ¦ This document is uncontrolled when printed. Refer to SharePoint for the latest version.
Calculation of Temperature Rise of Air Inside Enclosure
Project No: |  |  |  | Client/Order No: |  |  |  |  | Calculation No:
Project: | [8 empty] | Issue:
Date:
Compartment / Enclosure Reference:
| Compartment / Enclosure Dimensions: |  | Height | 1800 |  |  |  | mm
|  |  | Width | 600 |  |  |  | mm
|  |  | Depth | 600 |  |  |  | mm
| Efffective Cooling Surface |  |  | Dimensions |  |  | Ao |  | Surface Factor b | Ao X b
|  |  |  | (m x m) |  |  | m |  | according to Table I
|  | Top |  | 0.6 | x | 0.6 | 0.36 |  | 0.7 | 0.252
|  | Front |  | 1.8 | x | 0.6 | 1.08 |  | 0.9 | 0.972
|  | Rear |  | 1.8 | x | 0.6 | 1.08 |  | 0.5 | 0.54
|  | Left-Hand Side |  | 1.8 | x | 0.6 | 1.08 |  | 0.5 | 0.54
|  | Right-Hand Side |  | 1.8 | x | 0.6 | 1.08 |  | 0.5 | 0.54
|  | Ae: Effective Cooling Surface = S(Ao X b) = | [7 empty] | 2.844
| Enlcosure Temperature Rise Calculation | P: Power Dissipate Within Enlcosure By Components (W) | [7 empty] | 200
|  | K: Heat exchange coefficient (W/m2 K ) | [7 empty] | 5.5
|  | Temperature Rise Within Enlcosure (K) | [7 empty] | 12.7861
| Required Air Flow Calculation (If Necessary) | Maxium Permitted Temperature Rise (degC) | [7 empty] | 10
|  | Pe: Amount of Heat Enclosure Can Dissipate (W) | [7 empty] | 156.42
|  | Qv: Amount of Watts to be Remove By Forced Venilation (W) | [7 empty] | 43.58
|  | f: Constant (m3 K/Wh) | [7 empty] | 3.1
|  | V: Required Air Flow (m3/h) | [7 empty] | 13.5098
Conclusion The following fan and filter combination is required to meet the above criteria.
| Calculated By: | [6 empty] | Signed:
| Approved By: | [6 empty] | Signed:
2
DT :
DT :

## Table I
Document Reference: 02-05-19-14 ¦ Version 1.0 ¦ This document is uncontrolled when printed. Refer to SharePoint for the latest version.
SURFACE FACTOR TABLE 1
Type of Installation | Surface Factor b
Exposed Top Surface | 1.4
Covered Top Surface | 0.7
Exposed Side Surfaces eg Front, Rear & Side Walls | 0.9
Coverd Side Surfaces | 0.5
Floor Surface | N.A.