| Project Ref: |  |
| --- | --- |
| Project Title: |  |

| BS EN 61439-2 Design Verification (LV Assemblies) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Characteristic to be verified | D.V. Clause | Enclosure System: Document Ref. | Document Ref. | BS EN 61439-2 Constructional / performance clause(s) |
| 1 | Strength of materials and parts Resistance to corrosion Thermal stability Resistance to abnormal heat and fire due to internal electric effects Lifting Mechanical impact Marking | 10.2 10.2.2 10.2.3.1 10.2.3.2 10.2.5 10.2.6 10.2.7 | Refer to enclosure technical documentation | LV Verification & Conformity Manual (DV-01) | 8.1.2 8.1.3.1 8.1.3.2 8.1.6 8.2.1 |
| 2 | Degree of protection of enclosures | 10.3 | Refer to enclosure technical documentation | LV Verification & Conformity Manual (DV-02) | 8.2.2, 8.2.3, 8.4.2.3, 8.2.101, 8.101 |
| 3 | Clearances | 10.4 | Refer to enclosure technical documentation | LV Verification & Conformity Manual (DV-03) | 8.3.2 Table 1 |
| 4 | Creepage distances | 10.4 | Refer to enclosure technical documentation | LV Verification & Conformity Manual (DV-03) | 8.3.3 Table 2 |
| 5 | Protection against electric shock and integrity of protective circuits: | 10.5 |  |  |  |
|  | Effective continuity between the exposed conductive parts of the assembly and the protective circuit | 10.5.2 | Refer to enclosure technical documentation | LV Verification & Conformity Manual (DV-04) | 8.4.3.2.2 |
|  | Short-circuit withstand strength of the protective circuit | 10.5.3 |  |  | 8.4.3.2.3 |
| 6 | Incorporation of switching devices and components | 10.6 | N/A | LV Verification & Conformity Manual (DV-05) | 8.5 |
| 7 | Internal electrical circuits and connections | 10.7 | N/A | LV Verification & Conformity Manual (DV-06) | 8.6 |
| 8 | Terminals for external conductors | 10.8 | N/A | LV Verification & Conformity Manual (DV-07) | 8.8 |
| 9 | Dielectric properties: | 10.9 | Refer to enclosure technical documentation | LV Verification & Conformity Manual (DV-08) | 9.1.2 Table 8 |
|  | Power-frequency withstand voltage | 10.9.2 |  |  |  |
|  | Impulse withstand voltage | 10.9.3 |  |  | 9.1.3 Table 9 |
| 10 | Temperature-rise limits | 10.10 | Refer to enclosure technical documentation | LV Verification & Conformity Manual (DV-09) | 9.2 Table 6 |
| 11 | Short-circuit withstand strength | 10.11 | Refer to enclosure technical documentation | LV Verification & Conformity Manual (DV-10) | 9.3 Table 13 |
| 12 | Electromagnetic compatibility (EMC) | 10.12 | N/A | LV Verification & Conformity Manual (DV-11) | J.9.4 (Annex J) |
| 13 | Mechanical operation | 10.13 | N/A | LV Verification & Conformity Manual (DV-12) | 8.1.5 |

| Conformity assessment complete and CoC validated: | LV Design Engineer: | Date: | Signature: |
| --- | --- | --- | --- |