Scope of Works - Ductwork

All works are to be carried out in accordance with the Contract requirements, including the latest British Standards & Regulations.

This package-specific scope document is to be read in conjunction with all documents referenced within the sub-contract order.

General

The Sub-Contractor shall ensure that no Prohibited Materials are used or incorporated in the Sub-Contract Works.

All works to be fully compliant with all documentation referenced within the Sub-Contract order.

Package Scope of Work

The following is an outline scope of work only and the Sub-Contractor is therefore required to refer to all drawings, specifications, contractor’s proposals and other relevant sections of the sub-contract documentation for complete details of the scope of work.

The works include (but not limited to) the manufacture, supply, delivery, offloading / distribution to workface, installation, erection and testing of the complete ductwork installation including all necessary bracketry, supports, flexible ductwork, plenum boxes and all other items required to provide a complete and fully compliant ductwork installation in accordance with all current regulations, specifications, drawings and supplementary correspondence referred to herein.

Provision of all necessary management, supervision, labour, plant, materials, equipment, tools, consumables, ancillaries, access equipment, MEWPS and liaison with the builder / any other trades necessary  to carry out the works.

The Sub-contractor will be responsible for the offloading, distribution, positioning and installation of all duct mounted equipment including (but not limited to):

- Fans

- Attenuators

- Fan Coil Units

- Heater / cooling batteries

- Smoke / Fire Dampers

- Grilles / Diffusers

- Plenums

- VAV

- Filters

- AHU’s (bolting together and all ductwork connections)

- Any transformation Pieces Required

Access doors are to be provided at all dampers, turning veins, heater batteries or any other duct mounted equipment plus additional hatches to permit easy access for cleaning as per TR19 Level 3.

All ducts to be sealed where they exit the building to permit a building air-tightness test to be carried out by others.

Should steel wire supports be used only GRIPPLE products and relevant data sheets provided for approval (corner inserts will be required on all rectangular ductwork).

Ductwork installation to conform to DW144, and be in accordance with TR19, PDI Level 1.

Fan coil / ceiling cassette units shall be mounted in such a way that they can be moved to suit the requirements of the ceilings grid, both horizontally and vertically, where appropriate. All Fan coil units shall be supported by a rigid method (screwed rod), NOT GRIPPLE.

Fire & Fire & Smoke dampers are to be supplied to suit the fire strategy & consultant’s ventilation drawings, not one or the other.

All flexible connections are to be no longer than 500mm.

Manufacturing drawings are to include invert levels as well as any relevant notes that will aid the installation process. Final co-ordination with all services is to remain the responsibility of the sub-contractor and any co -ordination need to be raised for review with the site team.

The Sub-contractor shall include for all works and materials allied and incidental, which are not explicitly specified, but, which are necessary to complete the installation as a working whole.

All material is to be stored and protected against damage either physical or weather ingress damage.

The sub-contractor is responsible for the protection of their works against damage until such time that PC is achieved. It shall not be the responsibility of COMPANY NAME, nor its other subcontractors, to do so.

The sub-contractors price shall be in full compliance with the enclosed specification & CP, s taking note of all its particular requirements over and above that which would normally be expected.

The subcontractor has allowed to provide all fixings, fixings to be suitable for application, environment and building fabric.

The sub-contractor has included for all access equipment to enable safe installation of the works, including those at high level.

Work areas to be left clean and tidy at the end of each shift. / Clean as you go, the main contractor will be enforcing this and charges may be applied for non-conformance. The main contractor will not be providing skips on this project and it is therefore your responsibility to remove your own rubbish at the end of each working day at your own cost.

The works are to be carried out in a manner and sequence that fully coordinates with the main construction program and with all other services within the building construction, prior to commencing the works a fully detailed programme of works is to be submitted for our review inclusive of the projected labour in the form of a labour histogram for each discipline.

All works are to be carried out under the Construction (Design & Management) Regulations, and you shall have made all necessary allowances as required under the said regulations to carry out these works.

All work carried out under this contract are to be executed in the manner set out as above and in full compliance with current legislation and codes of practice, to the complete satisfaction of relevant industry standards.

All work should conform to the best principles of modern practice and should be carried out by fully competent tradesperson of appropriate grades, under skilled supervision SSSTS. It is your responsibility to provide a SSSTS supervisor for every 10no. men that you have working on the project, COMPANY NAME will not be providing such a facility on your behalf.

All work should conform to the best principles of modern practice and should be carried out by fully competent tradesperson’s who hold the appropriate grades and relevant CSCS skill card.

The works are to be supervised at all times by a skilled supervisor SSSTS who is a direct employee, in addition to the supervisor duties your supervisor will be required to attend daily safe start meetings and also liaise with our site representative on a daily basis and may be called to attend ongoing program and coordination meetings at a site level.

Subcontractor supervisor to attend health & safety meetings as required to highlight daily H&S Issues.

Certification and fully detailed information for inclusion within the operating and maintenance manuals are to be provided for each element. Noting operating manuals and as fitted drawings are to be made available no later than 2 weeks prior to PC.

The subcontract price is deemed to have included for all fittings and fixings including but not limited to bends, tees, branches, reducers, turning vanes, access doors, brackets, flanges, nuts and bolts etc. that are required for proper systems installation and performance even if these are not shown on drawings issued as part of the Sub-Contract.