Project No.

Project Name

Maintenance Procedures SECTION 03

- 5.1 EQUIPMENT MAINTENANCE SHEETS

- 5.1.1 VRF AIR CONDITIONING EQUIPMENT

- 5.1.2 FANS (DIRECT DRIVE)

- 5.1.3 GRILLES & DIFFUSERS

- 5.1.4 DUCTWORK (INCLUDING DAMPERS)

- 5.1.5 HEAT RECOVERY VENTILATION UNITS

- 5.1.6 AIR SOURCE HEAT PUMP

- 5.1.7 HOT WATER STORAGE

WARNING

IT SHOULD BE REMEMBERED THAT WITH REMOTE CONTROLLED

SYSTEMS, VARIOUS ITEMS OF EQUIPMENT MAY BECOME ENERGISED

WITHOUT WARNING.

IT IS THEREFORE IMPERATIVE TO ENSURE THAT ANY ITEM OF

EQUIPMENT IS FULLY ISOLATED BEFORE ANY MAINTENANCE WORK

IS CARRIED OUT.

5.1 EQUIPMENT MAINTENANCE SHEETS

5.1.1 VRF AIR CONDITIONING EQUIPMENT

GENERAL MAINTENANCE REQUIREMENTS

a) Indoor Units (Or Evaporator Unit)

MAINTENANCE NOTES

Air conditioning units are sophisticated machines requiring special equipment for

maintenance of the refrigerant side. It is therefore strongly recommended that a

refrigeration specialist is employed to maintain the machine.

GENERAL MAINTENANCE REQUIREMENTS

Time Period Nature of Check.

Weekly

• Check unit is operating satisfactorily. Investigate any unusual noises or vibration.

Monthly

• Check units filter is clean and correctly located.

• Clean or replace as necessary

3 Monthly

• Check security of unit and from mountings.

•  Check cooling coils condensate collection tray is clean and drain line is unobstructed.

6 Monthly

• Clean impeller and blades. Check security of impeller on shaft and inspect blades for security and damage.

• Clean unit internally and inspect for corrosion to casing. Remedy any corrosion found.

2 Yearly

• Overhaul unit. By Specialist.

b) Condenser Unit

MAINTENANCE NOTES

Air cooled condensers are sophisticated machines requiring special equipment for

maintenance of the refrigerant side. It is therefore strongly recommended that a

refrigeration specialist is employed to maintain the machine.

GENERAL MAINTENANCE REQUIREMENTS

Time Period Nature of Check

Weekly

• Check air inlets and condenser fins are unobstructed.

• Check low ambient protection equipment is operating correctly.

3 Monthly

• Check the machine for refrigerant leaks and is fully charged.

• Clean condenser coil matrix.

• Use Vacuum Cleaner by Specialist.

Yearly

• Check overall unit for deterioration, noting particularly any signs of corrosion. Take any necessary remedial action. Consult manufacturer as to appropriate treatment.

As manufacturer’s recommendation

1. Overhaul compressor and refrigerant circuit in accordance with manufacturer’s instructions. By Specialist.

5.1.2 FANS (DIRECT DRIVE)

GENERAL MAINTENANCE REQUIREMENTS

Time Period Nature of Check

Daily

• Check fan is running smoothly without excessive noise or vibration.

Weekly

• Check flexible connections are secure, taut and airtight. Connections must not restrict air flow.

Monthly

• Check anti-vibration mountings/hangers are secure, free to move and in good condition.

6 Monthly

• Clean impeller and blades. Check security of impeller on shaft and inspect blades for security and damage.

• Check performance of fan (shaft speed, air velocity and pressure).

2 Yearly

• Clean and check casing externally, repairing any corrosion or damage to finish found. Check all bolted joints are secure.

5.1.3 GRILLES & DIFFUSERS

GENERAL MAINTENANCE REQUIREMENTS

Time Period Nature of Check

Weekly

• Check that grilles and diffusers are clean and not smutting surrounding surface.

3 Monthly

• (External louvres) Clean slats and mesh screen. Remove any debris found.

6 Monthly

• Measure air volume at each grille and compare with commissioning values. Check air diffusion pattern. Adjust if necessary. Any readjustment to air volumes should be carried out by specialists.

5.1.4 DUCTWORK (INCLUDING DAMPERS)

MAINTENANCE NOTES

It is imperative that all regulated settings of dampers are checked, marked and noted

so that they can be correctly reinstated if and when moved.

GENERAL MAINTENANCE REQUIREMENTS

Time Period Nature of Check

Monthly

• Check all duct joints and access panels are airtight. Reseal as necessary. Check all test hole plugs are in place.

• Check all regulating dampers are locked in regulated positions.

6 Monthly

• Operate dampers through total range of travel to check for freedom of movement. Where restrictions are found readjust or lubricate linkage as necessary. Return dampers to correct regulated positions.

• Test operation and sealing of each fire damper. Lubricate pivots and guides. Check fusible links are clean and positioned in air stream. This activity may be carried out with local fire officer.

• These checks may be subject to the requirements of the local fire brigade. Maintain a log of all fire dampers tested, record faults and any remedial action taken. This log should be maintained as proof to the local fire brigade that regular checks are maintained. If any fire dampers are inaccessible, advise client.

Yearly

• Clean damper blades and lubricate pivots linkage, checking for wear.

• Check all ductwork supports are tight and free of corrosion.

• Inspect ductwork for damage to finishes and corrosion. Treat and repair as necessary. Check the internal condition and cleanliness of the ductwork and clean where necessary. Additional guidance should be sought from HVCA TR/19 “Internal Cleanliness of Ventilation Systems”.

5.1.5 HEAT RECOVERY VENTILATION UNITS

FREQUENCY OF SYSTEM CHECKS

Time Period Nature of Check

Weekly

• Check unit is operating satisfactorily.

• Investigate any unusual noises or vibration.

Monthly

• Check if unit filter needs cleaning.

• Clean as necessary. (remove and use vacuum cleaner)

• On changing cells wipe any accumulated dirt from the retaining channels and frames.

• Check condensate collection tray is clean and drain line is unobstructed.

Annually

• Check heat recovery matrix and clean off any dust buildup with a vacuum cleaner.

• Clean unit internally.

5.1.6 AIR SOURCE HEAT PUMP

FREQUENCY OF SYSTEM CHECKS

b) Condenser Unit

MAINTENANCE NOTES

Air cooled condensers are sophisticated machines requiring special equipment for

maintenance of the refrigerant side. It is therefore strongly recommended that a refrigeration specialist is employed to maintain the machine.

GENERAL MAINTENANCE REQUIREMENTS

Time Period Nature of Check

Weekly

- Check air inlets and condenser fins are unobstructed.

- Check low ambient protection equipment is operating correctly.

3 Monthly

- Check the machine for refrigerant leaks and is fully charged.

- Clean condenser coil matrix.

- Use Vacuum Cleaner by Specialist.

Yearly

- Check overall unit for deterioration, noting particularly any signs of corrosion. Take any necessary remedial action. Consult manufacturer as to appropriate treatment.

As manufacturer’s recommendation

- Overhaul compressor and refrigerant circuit in accordance with

5.1.7 HOT WATER STORAGE

FREQUENCY OF SYSTEM CHECKS

Time Period Nature of Check

Weekly

• Check unit is operating satisfactorily.

• Check cylinder and components for leaks.

Monthly

- Clean as necessary.

- On changing cells wipe any accumulated dirt from the retaining channels and frames.

- Check cylinder and components for leaks.

Annually

• Check heat recovery matrix and clean off any dust buildup with a vacuum cleaner.

• Clean unit internally.

• Pump Maintenance Helpful Information (Refer to the Pump Specific Fault Diagnosis and Maintenance table in section

• Anode Plugs Four zinc anodes are mounted in the heater tank. These provide sacrificial corrosion protection to the system and will deteriorate. They should be inspected regularly and replaced when necessary.

• Heater Elements Heater element cover plates should be removed to check for leaks and, if necessary, check element insulation. To remove any elements, use WHE-3 element socket, always keep sufficient spare elements available.

• Maintenance Note Pressure irregularities are not a definitive diagnosis of pump faults, and it is essential to carry out full fault finding in order to maintain the unit operation. Before servicing the pump, it is prudent to carry out checks on the following:

• Inlet plumbing for size

• Restriction and/or air leaks

• Condition of the by-pass valve

• Condition of the pressure gauge

• Shut-off valves in the inlet or discharge plumbing to be sure they are fully open.