Internal Procedures

Section 5

High Voltage Electrical, Manufacturing

This document is uncontrolled when printed. Please refer to Sharepoint for the latest version.

VERSION

DATE

AUTHOR

REVIEWED BY

APPROVED BY

NEXT REVIEW DATE

DATE

AUTHOR

REVIEWED BY

APPROVED BY

NEXT REVIEW DATE

IP-01-09-01-05-V1

DOCUMENT REF

Contents

INTRODUCTION	2

HIGH VOLTAGE ELECTRICAL	3

MANUFACTURING	18

MANUFACTURING FLOWCHART – CONTROL PANELS & SWITCHGEAR	34

# INTRODUCTION

Our procedures exist for a reason. They protect our standards, our people and our reputation. At COMPANY NAME, following procedures isn’t about bureaucracy - it’s about delivering quality work with consistency and discipline. It reflects the pride we take in doing the job properly, the responsibility we have to our customers and colleagues and our commitment to continuous improvement.

Clear processes help us manage risk early, communicate effectively and ensure that no detail is overlooked. They create fairness, accountability and a shared way of working across the Group. Most importantly, they allow us to operate safely, professionally and profitably.

Everyone at COMPANY NAME is trusted to apply judgement within the framework we provide but that trust comes with the expectation that procedures are understood, followed and upheld. Doing so protects what makes us strong today and supports our progress for the future.

# HIGH VOLTAGE ELECTRICAL

NOTE

ENA SHE Standard 07 – Model Distribution Safety Rules shall remain the controlling safety standard for HV works covered by this procedure. This COMPANY NAME procedure is a supporting internal management procedure only and must be read and applied in conjunction with ENA SHE Standard 07. It must not be interpreted as replacing, reducing or amending the requirements of ENA SHE Standard 07. Where any conflict, ambiguity, omission or difference exists, ENA SHE Standard 07 shall always take precedence.

1. PURPOSE

To define the management controls, responsibilities and safe systems of work for all High Voltage electrical activities undertaken by COMPANY NAME or on behalf of COMPANY NAME.

2. SCOPE

This procedure applies to:

- HV electrical installations

- HV switching operations

- HV maintenance activities

- HV testing and commissioning

- HV cable works

- HV substations and switch rooms

- Transformers and associated HV equipment

- All COMPANY NAME employees and subcontractors engaged in HV works

This procedure applies to both permanent and temporary HV systems.

3. RESPONSIBILITIES

Director

- Ensure suitable resources and competent personnel are available

- Approve Senior Authorised Persons (SAPs)

- Ensure suitable arrangements are in place for HV safety management

Senior Authorised Person (SAP)

- Overall control of HV safety management

- Control all HV permits and switching activities

- Issue permits and sanctions

- Approve switching schedules

- Verify competency of HV personnel

- Ensure systems are safely returned to service

- Suspend works where unsafe conditions exist

- Ensure compliance with this procedure

Authorised Person (AP)

- Carry out HV switching operations

- Implement isolations and safety precautions

- Issue safety documentation where authorised

- Maintain switching records and communication logs

Competent Person (CP)

- Carry out work under permit

- Follow all instructions and safety controls

- Stop work immediately if unsafe conditions arise

- Maintain good housekeeping standards within work areas

Project Managers

- Ensure HV works are properly planned

- Ensure RAMS and permits are in place

- Ensure only approved personnel undertake HV activities

- Ensure suitable programme time is allocated for HV isolations and switching

- Coordinate with clients and DNOs where required

Health & Safety Manager

- Monitor compliance with HV procedures

- Review incidents and non-conformances

- Ensure HV training and authorisations remain current

- Carry out periodic audits and inspections

4. HV AUTHORISATION PROCESS

4.1 Competence Requirements

Personnel involved in HV works must demonstrate:

- Relevant HV qualifications

- Appropriate technical experience

- Understanding of HV safety rules

- Knowledge of switching procedures

- Understanding of permit systems

- Understanding of emergency and rescue procedures

- A valid, in date Competence Certificate clearly showing Authorisation level, voltage and operations.

4.2 Authorisation Levels

Authorisation levels may include:

- Senior Authorised Person (SAP)

- Authorised Person (AP)

- Competent Person (CP)

Authorisations:

- Shall be issued in writing

- SHall be restricted to specific voltages, operations or systems

- Shall be reviewed periodically

- May be withdrawn at any time by the company

Temporary authorisations shall be clearly defined and time limited.

4.3 Authorisation Register

The HV Authorisation Register shall be maintained by the Health & Safety Manager and shall include:

- Name

- Competency level

- Authorisation level

- Expiry date

- Restrictions

- Approved by

The register shall be treated as the primary control document for HV competency management.

4.4 Training

HV personnel shall undertake refresher training and reassessment at intervals not exceeding 3 years.

Training records and certificates shall be maintained within the employee training records.

5. GENERAL SAFETY RULES

- All HV apparatus shall be treated as LIVE until proven DEAD

- Safe isolation procedures shall always be followed

- Switching shall only be undertaken by authorised personnel

- Suitable PPE shall always be worn

- Access to HV rooms and substations shall be restricted

- All HV work shall be planned using ALARP principles

- All switching communications shall be recorded and read back

- All safety devices, notices and locks shall be controlled

- All persons shall stop work immediately if unsure of system status

- Minimum approach distances shall be maintained at all times

- Work areas shall be adequately controlled and barricaded where required

- Weather conditions shall be considered during external HV works

- All switching points shall be clearly identified prior to operation

6. ACCESS TO HV AREAS

6.1 Restricted Access

No person shall enter:

- HV substations

- HV switchrooms

- HV transformer compounds

- HV cable chambers

Unless:

- Authorised by a SAP or AP

- Have the competence to do so

- Accompanied by an authorised person where required

6.2 Key Control

HV room and substation keys shall:

- Be controlled by authorised personnel

- Be logged in a key register

- Not be duplicated without approval

- Remain secured when not in use

6.3 Visitors

Visitors shall:

- Sign in

- Receive a safety briefing

- Always remain under supervision

6.4 Housekeeping

- HV rooms shall remain locked when unattended

- Escape routes and access routes shall remain clear at all times

- Good housekeeping standards shall be maintained

7. HV SWITCHING OPERATIONS

7.1 Switching Control

All HV switching shall:

- Be planned in advance

- Be carried out using an approved switching schedule where required

- Be recorded within the switching logbook

- Be undertaken without unnecessary delay

Switching schedules shall be reviewed and approved by the SAP before implementation.

7.2 Communication

All switching instructions shall:

- Be read back

- Be confirmed

- Include equipment identification

- Be recorded where applicable

7.3 Switching Precautions

Before switching:

- Equipment condition shall be visually checked

- Correct equipment identification shall be confirmed

- Appropriate PPE shall be worn

- Abnormal conditions shall be reported immediately

Following switching:

- Equipment position shall be verified

- Switching records shall be completed immediately

7.4 Emergency Switching

Emergency switching shall:

- Be reported immediately to the SAP

- Be recorded

- Be reviewed following the event

- Be supported by a post-incident review where required

8. SAFE ISOLATION & EARTHING

8.1 Isolation

Before work commences the HV system shall:

- Be isolated from all sources of supply

- Be locked off

- Be labelled with caution and danger notices

- Be secured against inadvertent operation

8.2 Proving Dead

HV systems shall be proven dead using approved voltage testing equipment.

Voltage testing devices shall:

- Be checked before use

- Be checked after use

- Be suitable for the system voltage

8.3 Earthing

Circuit Main Earths and Additional Earths shall be applied where required.

Earthing equipment shall:

- Be visually inspected prior to use

- Be suitable for fault levels and system voltage

- Be applied only by authorised personnel

8.4 Key Safes & Safety Locks

Safety keys and locks shall:

- Remain under SAP/AP control

- Be uniquely identifiable

- Be logged and controlled

8.5 Re-Energisation

Re-energisation shall only take place:

- Following permit cancellation

- Following completion checks

- With SAP approval

8.6 Return to Service

Before returning HV equipment to service:

- All permits shall be cancelled

- All persons shall be accounted for

- All earths shall be removed

- All tools and temporary equipment shall be removed

- Guards and covers shall be reinstated

- The SAP/AP shall confirm the system is safe to energise

9. SAFETY DOCUMENTATION

The following safety documents shall be used where applicable:

- HV Permit to Work

- Sanction for Test

- Limitation of Access

- Permit to Energise

- Permit for Isolation

- Switching Schedule

- HV Access Permit

The permit register shall be maintained as the primary control document.

All completed permits and safety documents shall be retained within the project records.

10. TESTING & COMMISSIONING

10.1 General

Testing and commissioning shall:

- Be undertaken by competent personnel

- Follow approved procedures

- Use calibrated test equipment

- Be planned and supervised appropriately

10.2 Sanction for Test

Testing on previously energised equipment shall:

- Require a Sanction for Test

- Be controlled by a SAP

- Be supported by suitable RAMS

10.3 Commissioning Records

Commissioning documentation shall include:

- Test certificates

- Protection settings

- Functional testing

- Energisation records

- Calibration information where applicable

10.4 Energisation

Before energisation:

- All persons shall be clear of danger

- Temporary supplies shall be identified and controlled

- System integrity shall be confirmed

11. HV CABLE WORKS

- All HV cables shall be treated as LIVE until positively identified and proven DEAD

- Cable identification and spiking procedures shall be followed

- Excavation near HV cables shall follow approved procedures

- Induced voltages and sheath voltages shall be considered

- Cable routes shall be verified before excavation works commence

- Drawings and cable detection equipment shall be used to verify routes

- Hand digging requirements shall be identified within RAMS

- Damaged cables shall be treated as LIVE until proven otherwise

12. TRANSFORMERS & HV EQUIPMENT

Before work on transformers:

- HV and LV supplies shall be isolated

- Appropriate earthing arrangements shall be applied

- Associated LV systems shall be secured

- Suitable caution and danger notices shall be displayed

Static capacitors and associated equipment shall:

- Be discharged

- Be earthed

- Remain short circuited where removed from service

13. PERSONAL PROTECTIVE EQUIPMENT (PPE)

The following minimum PPE shall be considered for HV works:

- Arc flash rated clothing

- HV gloves where applicable

- Safety helmet

- Eye protection

- Safety footwear

- Face shields where required

PPE requirements shall be defined within RAMS and task risk assessments.

- PPE shall be inspected prior to use

- Damaged PPE shall be removed from service immediately

- Arc flash PPE levels shall be determined through risk assessment

14. RISK ASSESSMENT & RAMS

- All HV activities shall have suitable RAMS

- RAMS shall be reviewed prior to commencement

- Residual risks shall be communicated to all personnel

- Dynamic risk assessments shall be undertaken where conditions change

- Emergency arrangements shall be briefed before work commences

- Subcontractor RAMS shall be reviewed using: 02-03-41 – Subcontractor RAMS Review Form

15. SUBCONTRACTORS

Only approved subcontractors may undertake HV works.

Subcontractors must:

- Be approved in accordance with Section 9 – Company Engineers & Subcontractors

- Provide evidence of HV competency

- Provide valid insurance

- Provide suitable RAMS

- Comply with COMPANY NAME HV procedures and permit controls

HV subcontractors shall not commence work until formally approved.

16. INCIDENTS & EMERGENCIES

All HV incidents, near misses or dangerous occurrences shall:

- Be reported immediately

- Be investigated

- Be reviewed by the Health & Safety Manager

- Be escalated to senior management where required

Emergency procedures shall include:

- Electric shock response

- Arc flash incidents

- Fire response

- Emergency isolation arrangements

- Emergency rescue arrangements

Lessons learned shall be communicated where appropriate.

Emergency rescue equipment shall be periodically inspected.

17. HV Emergency & Rescue Arrangement

- Stop working immediately

- Do not touch casualty until system is isolated

- Initiate emergency isolation

- Contact emergency services

- Apply first aid/CPR if safe

- Secure area and prevent re-energisation

- Report incident immediately

- Ensure rescue equipment is available before work commences

18. RECORDS & DOCUMENT CONTROL

The following records shall be maintained:

- 02-05-18-01 – Permit to Work

- 02-05-18-02 – HV Sanction For Test

- 02-05-18-03 – HV Limitation of Access

- 02-05-18-04 - HV Permit to Energise

- 02-05-18-05 – HV Registers & Logs

- 02-05-18-06 – Energisation Certificate

- Test and commissioning records

- HV maintenance records

- HV training records

- Inspection records

- RAMS and risk assessments

All records shall be stored within the project folder structure and SharePoint.

Records shall remain legible, identifiable and retrievable.

19. MONITORING & REVIEW

- HV procedures shall be audited periodically

- Authorisations shall be reviewed annually

- Switching records shall be reviewed monthly

- Lessons learned shall be communicated across the business

- Spot inspections may be carried out during HV works

- Permit compliance may be audited periodically

- Findings and corrective actions shall be recorded and tracked

- This procedure shall be reviewed annually or following any significant incident or legislative change

20. REFERENCES

- Electricity at Work Regulations 1989

- BS 7671

- ENA SHE Standard 07 – Model Distribution Safety Rules

- HSE GS38

- Section 4 – Design & Project Management

- Section 7 – Health & Safety

- Section 8 – Training

- Section 9 – Company Engineers & Subcontractors

21. KEY PRINCIPLES

- HV systems shall always be treated as dangerous

- Competence and authorisation are mandatory

- Safe isolation and earthing are critical controls

- Permit systems shall always be followed

- No live working is permitted

- No uncontrolled live working is permitted

- Safety takes priority over programme or commercial pressures

- Personnel shall stop work if unsafe conditions arise

- Clear communication and supervision are essential

Guidance Sources Used

This procedure was developed using the existing COMPANY NAME procedures and the ENA SHE Standard 07 Model Distribution Safety Rules as guidance.

# MANUFACTURING

1. Purpose

To ensure LV Assemblies including Motor Control Centers (MCCs) LV control panels and LV switchgear manufactured by COMPANY NAME are designed, procured, assembled, inspected, tested, documented, approved and handed over in a controlled, consistent and auditable manner.

The purpose of this procedure is to ensure that customer requirements are understood before manufacturing starts, design information is checked and approved before build, materials and components are suitable and traceable, manufacturing is completed to approved drawings and specifications, inspection and testing are completed at defined stages, defects are recorded and closed out, and final equipment is safe, compliant, labelled, documented and ready for installation or delivery.

This procedure should be read alongside the LV Operations Manual and the LV Verification and Conformity Manual, which together detail the end-to-end processes and standards for certified LV Assemblies.

2. Scope

- Bespoke control panels

- Process control panels

- Motor control Centres

- PLC panels

- HMI panels

- BMS / controls panels

- Instrumentation and I/O panels

- Power distribution panels

- LV switchgear assemblies

- Form 4 compartmentalised LV Assemblies

- Modifications to existing panels or switchgear

- Factory acceptance testing

- Manufacturing handover documentation

3. Responsibilities

Manufacturing Manager / Workshop Manager

- Manage the manufacturing process from receipt of approved design through to final handover

- Ensure manufacturing work is planned, resourced and controlled

- Ensure the manufacturing job pack is created and maintained

- Ensure only competent personnel undertake manufacturing, wiring, inspection and testing activities

- Ensure stage inspections and sign-offs are completed

- Ensure defects and non-conformances are recorded and closed out

- Ensure completed panels and switchgear are protected, packaged and dispatched correctly

Design Manager / Controls Engineer / Electrical Design Engineer

- Review customer requirements, specifications and design inputs

- Produce or check design drawings, schematics, panel layouts and associated schedules

- Ensure the design is suitable for the intended use and environment

- Confirm applicable standards, client requirements and technical requirements

- Complete design reviews and approve information for manufacture

- Review design changes and ensure drawings and schedules remain current

Project Manager / Account Manager

- Confirm the customer requirements, scope, programme and delivery expectations

- Ensure the manufacturing team receives the latest approved information

- Coordinate client approvals, technical submissions and customer witness testing where required

- Ensure commercial or programme impacts from design or manufacturing changes are managed

- Coordinate installation, commissioning and handover requirements

Panel Builder / Wire Person / Manufacturing Operative

- Manufacture equipment in accordance with approved drawings, schedules, specifications and this procedure

- Use suitable tools, equipment and PPE

- Maintain good workmanship and housekeeping standards

- Raise queries where information is missing, unclear or conflicting

- Stop work where there is a risk of error, unsafe condition or non-conformance

- Complete required in-process checks and records

Tester / Commissioning Engineer

- Complete inspection, electrical testing and functional testing

- Ensure test equipment is suitable and calibrated where required

- Record test results accurately

- Identify and record defects, snags and non-conformances

- Confirm when equipment is safe and ready for FAT, dispatch or installation

Purchasing / Stores

- Procure components in accordance with approved bills of materials and purchasing procedures

- Ensure materials are checked on receipt

- Ensure substitutions are not made without technical approval

- Maintain traceability where required

- Ensure non-conforming or damaged components are quarantined and reported

QA Manager / QA Administrator

- Ensure controlled documents, checklists and records are maintained

- Support audits of the manufacturing process

- Ensure completed manufacturing records are stored in the correct SharePoint location

- Ensure any non-conformances are recorded and closed out in accordance with the Quality Procedure

Health & Safety Manager

- Support workshop risk assessments and manufacturing health and safety controls

- Ensure relevant training and competency requirements are included in the Training Matrix

- Review accidents, incidents, near misses and significant non-conformances

4. Procedure / Process

4.1 Manufacturing Enquiry / Order Review

Before manufacturing starts, the Manufacturing Manager and/or Project Manager shall review the order, scope and customer requirements. The review shall confirm:

- Customer name and project reference

- Equipment type and quantity

- Delivery date and programme requirements

- Specification and drawings received

- Technical requirements

- Applicable standards and client requirements

- Design responsibility

- Testing and witnessing requirements

- Documentation requirements

- Delivery, packaging and installation requirements

- Any commercial or programme constraints

- Where information is incomplete, unclear or contradictory, the issue shall be raised and resolved before proceeding to the next stage.

4.2 Manufacturing Job Pack

A manufacturing job pack shall be created for each panel, switchgear assembly or batch of equipment. The job pack shall include, where applicable:

- Customer order / instruction

- Project reference

- Approved drawings

- Electrical schematics

- General arrangement drawings

- Panel layout drawings

- Door layout drawings

- Bill of materials

- Cable schedules

- Terminal schedules

- I/O schedules

- PLC / HMI information

- Functional Design Specification

- Technical submissions

- Risk assessments / RAMS where required

- Inspection and test plans

- Stage checklists

- FAT requirements

- Client witness requirements

- Defect / snag records

- Handover documentation checklist

4.3 Design Input Review

A design input review shall be completed before detailed manufacturing drawings are released for build. The review shall consider:

- Customer specification

- Process requirements

- Control philosophy

- Equipment to be controlled

- Operating environment

- Incoming supply details

- Fault level / short circuit requirements where applicable

- IP rating

- Form of separation where applicable

- Heat dissipation / ventilation requirements

- Cable entry arrangements

- Space for installation and maintenance

- Labelling requirements

- Safety and emergency stop requirements

- Functional safety requirements where applicable

- Interface requirements with other systems

- Remote monitoring / communications requirements

- Cyber security or network requirements where applicable

4.4 Applicable Standards and Compliance Review

The applicable standards, statutory requirements and customer requirements shall be identified for each manufacturing project. These may include, where applicable:

- BS EN 61439 series for LV switchgear and controlgear assemblies

- BS EN 60204-1 for electrical equipment of machinery

- BS 7671 where installation wiring requirements apply

- Electricity at Work Regulations

- Supply of Machinery / UKCA / CE requirements where applicable

- EMC requirements where applicable

- Functional safety requirements where safety-related control functions are included

- Client-specific standards and specifications

4.5 Design Development

- General arrangement drawing

- Panel layout drawing

- Door layout drawing

- Electrical schematics

- Single line diagram

- Power wiring diagrams

- Control wiring diagrams

- Terminal schedules

- Cable schedules

- I/O schedules

- Bill of materials

- PLC / HMI configuration notes

- Functional Design Specification

- Network architecture

- Instrument loop drawings where required

- Labelling schedule

- Heat loss / ventilation assessment where required

- Short circuit / rating information where required

4.6 Design Review and Approval for Manufacture

Before manufacture starts, the design shall be reviewed and approved. The design review shall confirm:

- The design matches the customer requirement

- The panel or switchgear arrangement is suitable

- Component selection is suitable

- Cable sizing and protective devices are suitable

- Labelling and terminal references are clear

- Access and maintenance requirements are considered

- Heat dissipation and ventilation are adequate

- Segregation between power, control, ELV, communication and safety circuits is suitable

- Drawings and schedules are complete enough for manufacture

- Testing and FAT requirements are defined

Where information is incomplete, unclear or contradictory, the issue shall be raised and resolved before proceeding to the next stage.

4.7 Procurement and Material Control

Materials and components shall be procured in accordance with the approved bill of materials and purchasing procedures. The following controls shall apply:

- Components shall match the approved design and specification

- Substitutions shall not be made without technical approval

- Critical components shall be checked against rating, voltage, current, breaking capacity, environmental suitability and compatibility

- Delivery notes shall be checked against orders

- Damaged or incorrect components shall be quarantined and reported

- Long lead items shall be monitored against programme requirements

- Material shortages shall be escalated immediately

4.8 Pre-Build Review

Before physical build starts, the Manufacturing Manager or nominated competent person shall complete a pre-build review. The pre-build review shall confirm:

- Latest drawings are available

- Bill of materials is available

- Major components are available

- Enclosure size and rating are correct

- Special tools or equipment are available

- Workshop resources are available

- Build sequence is understood

- Required stage inspections are identified

- Testing and FAT requirements are understood

- Any client witness points are identified

Where information is incomplete, unclear or contradictory, the issue shall be raised and resolved before proceeding to the next stage.

4.9 Mechanical Build and Enclosure Assembly

- Enclosure type, size and IP rating

- Mounting plates and gland plates

- Door furniture and hinges

- Locks and handles

- Ventilation, fans, filters or heaters where required

- Component positioning

- Trunking and DIN rail arrangement

- Busbar or distribution arrangement where applicable

- Cable entry and gland positions

- Sharp edges removed

- Paintwork and enclosure finish protected

- Earthing and bonding points provided

- Space for installation, access and maintenance

4.10 Wiring and Internal Assembly

- Correct cable type, colour and size

- Correct ferruling and identification

- Correct terminal references

- Segregation of power, control, ELV, communication and safety circuits

- Correct routing and support of wiring

- Correct termination of screened cables

- Correct earthing and bonding

- Tightness of terminals and fixings

- Torque settings applied where required

- No exposed conductors or loose strands

- Correct installation of protective devices

- Correct installation of relays, contactors, PLCs, HMIs, drives and instruments

- Correct labelling of devices, terminals and wires

4.11 Switchgear Specific Controls

- Assembly rating

- Incoming supply rating

- Short circuit withstand / fault level requirements

- Busbar rating and arrangement

- Protective device breaking capacity

- Selectivity / discrimination where required

- Form of separation

- Earthing and bonding arrangement

- IP rating

- Mechanical interlocking

- Shrouding and barriers

- Neutral and earth bar sizing

- Cable access and glanding space

- Labelling and warning notices

- Thermal performance / ventilation

- Routine verification requirements

- Operation of switching devices

4.12 Control Panel Specific Controls

- Control philosophy

- Process line operation

- PLC / HMI requirements

- Safety interlocks

- Emergency stop and reset arrangements

- Fail-safe states

- Alarm and fault indication

- Manual / auto operation

- Local / remote operation

- Instrumentation interfaces

- Communications and network interfaces

- I/O addressing

- Field wiring terminals

- Remote access requirements where applicable

- Customer operator requirements

- Maintenance and diagnostic access

4.13 Software, PLC, HMI and Controls Configuration

- Software version identification

- Backup of final programme / configuration

- Approved control philosophy

- I/O checks

- Functional testing

- Alarm testing

- Interlock testing

- User access / password control where required

- HMI screen review

- Customer naming conventions where required

- Final software backup stored with the manufacturing records

4.14 Inspection and Routine Verification

- Visual inspection

- Dimensional checks where required

- Component verification against drawings and bill of materials

- Labelling checks

- Continuity of protective bonding circuit

- Insulation resistance testing

- Polarity checks

- Control circuit checks

- Point-to-point wiring checks

- Functional operation testing

- Protective device checks

- Door interlock checks where applicable

- Emergency stop checks where applicable

- PLC / HMI function checks where applicable

- Verification of warning labels and safety notices

- Verification that covers, shrouds and barriers are fitted

Where information is incomplete, unclear or contradictory, the issue shall be raised and resolved before proceeding to the next stage.

4.15 Factory Acceptance Testing (FAT)

A Factory Acceptance Test shall be completed where required by the customer, specification, project risk or internal decision. The FAT may include:

- Visual inspection

- Verification against approved drawings

- Power-up checks where safe and applicable

- Control circuit testing

- Functional sequence testing

- Alarm and trip testing

- PLC / HMI demonstration

- Simulation of inputs and outputs

- Operator control checks

- Safety function checks where applicable

- Customer witness testing where required

- Review of documentation and labels

Where information is incomplete, unclear or contradictory, the issue shall be raised and resolved before proceeding to the next stage.

4.16 Energised Testing

Energised testing shall only be carried out where necessary and where suitable controls are in place. Before energised testing commences:

- The test area shall be controlled

- Only authorised and competent personnel shall be involved

- Suitable warning signs and barriers shall be used

- Emergency arrangements shall be understood

- Test equipment shall be suitable

- Exposed live parts shall be controlled

- The test shall be risk assessed

4.17 Defects, Snags and Non-Conformances

- Item number

- Description of issue

- Date identified

- Person identifying issue

- Responsible person

- Corrective action required

- Target close-out date

- Completion evidence

- Close-out signature

4.18 Design and Manufacturing Changes

- Technical impact

- Safety impact

- Cost impact

- Programme impact

- Documentation impact

- Need for customer approval

- Need to update drawings, schedules, software or technical file

Where information is incomplete, unclear or contradictory, the issue shall be raised and resolved before proceeding to the next stage.

4.19 Labelling, Identification and Warning Notices

- Panel name / reference

- Manufacturer details

- Serial number

- Rating plate

- Supply voltage

- Current rating

- Short circuit rating where applicable

- IP rating where applicable

- Warning labels

- Isolation labels

- Terminal identification

- Device labels

- Cable labels

- Door labels

- Functional labels for switches, indicators and controls

4.20 Documentation and Technical File

- Approved drawings

- As-built drawings

- Electrical schematics

- General arrangement drawings

- Bill of materials

- Test certificates

- FAT record

- Routine verification record

- Declaration of conformity / incorporation where applicable

- Technical file information where applicable

- PLC / HMI backup where applicable

- O&M information

- Component manuals

- Warranty information

- Recommended spares list where applicable

- Snag close-out record

4.21 Packing, Storage and Dispatch

- Equipment cleaned

- Loose items removed or secured

- Components protected

- Doors secured

- Keys and accessories bagged and labelled

- Documentation packed or issued electronically

- Transport protection applied

- Lifting points identified where applicable

- Delivery address confirmed

- Delivery date confirmed

- Photos taken before dispatch where required

4.22 Installation and Commissioning Interface

- As-built drawings

- Cable entry requirements

- Lifting and handling requirements

- Installation limitations

- Commissioning requirements

- Special tools or software requirements

- Known residual risks

- Open actions agreed for site completion

4.23 Handover and Close Out

- Equipment has been completed

- Inspections and tests have been completed

- FAT has been completed where required

- Snags and non-conformances have been closed or formally accepted

- Documentation has been issued

- Photographs have been saved where required

- Delivery / collection records are complete

- Customer or project handover is complete

Where information is incomplete, unclear or contradictory, the issue shall be raised and resolved before proceeding to the next stage.

4.24 Post-Manufacture Review

A post-manufacture review shall be considered for:

- Significant projects

- First-of-type panels or switchgear

- Repeat defects

- Customer complaints

- Programme delays

- Safety concerns

- High-value equipment

- New designs or new customers

5. Stage Gates and Sign-Off Requirements

Manufacturing shall include defined stage gates. No equipment shall be dispatched until all required inspections, testing, documentation and approvals have been completed or formally accepted by the responsible person.

| Stage Gate | Description | Sign-Off By |
| --- | --- | --- |
| Gate 1 | Order / design input review complete | Project Manager / Design Engineer |
| Gate 2 | Design approved for manufacture | Design Manager / Competent Engineer |
| Gate 3 | Materials and procurement checked | Manufacturing Manager / Stores |
| Gate 4 | Pre-build review complete | Manufacturing Manager |
| Gate 5 | Mechanical assembly inspection complete | Manufacturing Manager / QA |
| Gate 6 | Wiring inspection complete | Competent Tester / QA |
| Gate 7 | Electrical testing complete | Competent Tester |
| Gate 8 | Functional test / FAT complete | Tester / Project Manager / Client where required |
| Gate 9 | Documentation and handover pack complete | Manufacturing Manager / QA |
| Gate 10 | Dispatch approved | Manufacturing Manager |

6. Compliance / Key Rules

- No manufacturing shall commence without sufficient approved information

- The latest approved revision of drawings and schedules must be used

- Design changes must be controlled and recorded

- Component substitutions require technical approval

- Inspection and testing must be completed before dispatch

- Defects and non-conformances must be recorded and closed out

- FAT must be completed where required by customer, specification or project risk

- Energised testing must be controlled and risk assessed

- HV-related works must comply with the High Voltage Electrical Procedure

- Completed records must be saved in the correct SharePoint location

- Equipment must not be dispatched until the responsible person has approved release

7. Records / Documentation

| Reference | Document |
| --- | --- |
| 02-05-19-01 | Manufacturing Job Pack / Index Sheet |
| 02-05-19-02 | Design Input Review Checklist |
| 02-05-19-03 | Control Panel Design Review & Sign-Off |
| 02-05-19-04 | Switchgear Design Review & Sign-Off |
| 02-05-19-05 | Manufacturing Build Checklist |
| 02-05-19-06 | Wiring & Internal Assembly Inspection Checklist |
| 02-05-19-07 | Routine Verification / Electrical Test Record |
| 02-05-19-08 | Functional Test & FAT Record |
| 02-05-19-09 | Manufacturing Snag / Non-Conformance Register |
| 02-05-19-10 | Packing, Dispatch & Delivery Checklist |
| 02-05-19-11 | Manufacturing Handover Pack Checklist |
| 02-05-19-12 | Manufacturing Register |
| 02-05-19-13 | Bill of materials |
| 02-05-19-14 | Temperature Rise Calculations |
| 02-05-19-15 | Steelwork Delivery Checklist |
| 02-05-19-16 | Design Verification |
| 02-05-19-17 | UK Declaration of Conformity |
| 02-05-19-18 | EU Declaration of Conformity |
| 02-05-19-19 | Torque Record Checklist |

8. Monitoring & Review

The Manufacturing Manager shall monitor manufacturing programme performance, design release status, procurement status, build progress, inspection and test completion, snag and defect trends, customer witness requirements and dispatch readiness. The QA Manager and/or Health & Safety Manager may complete periodic audits of manufacturing records, workshop controls and completed equipment. Manufacturing performance shall be reviewed where repeated issues, complaints, defects or delays occur.

9. References

- Section 1 - Introduction, Quality Management & Procedure Control

- Section 3 - Estimating, Purchasing

- Section 4 - Design, Project Management

- Section 5 - High Voltage Electrical

- Section 7 - Environmental, Health & Safety

- Section 8 - Training

- Section 9 - Company Engineers & Subcontractors, Vehicles, Company & Hire Equipment

- Section 10 - Information Technology, Cyber Security, Data Protection

- Electricity at Work Regulations

- BS EN 61439 series where applicable

- BS EN 60204-1 where applicable

- BS 7671 where applicable

- UKCA / CE marking requirements where applicable

- Customer specifications and project requirements

10. Key Principles

- Build from approved information only

- Check early, do not rely on final inspection

- Record sign-offs at key stages

- Control design changes and component substitutions

- Test before dispatch

- Keep documentation current and auditable

- Treat manufacturing as an engineering quality process, not just a workshop activity

- Never compromise safety, compliance or workmanship for programme pressure

This flowchart is a condensed guide only. The full procedure must be read, understood and followed.

1. Order / Manufacturing Requirement Received

Gate 1 – Order / Design Input Review Complete

Review the customer order, project requirements, specification, drawings, programme and manufacturing scope.

Confirm:

- customer and project details

- type of control panel / switchgear required

- delivery requirements

- applicable specification

- design responsibility

- testing / FAT requirements

- documentation requirements

- any customer or site-specific requirements

No manufacturing shall proceed until the order and design inputs have been reviewed and there is sufficient information to define what is being built.

MANUFACTURING FLOWCHART – CONTROL PANELS & SWITCHGEAR

7. Mechanical Build / Enclosure Assembly

Gate 5 – Mechanical Assembly Inspection Complete

Manufacture the mechanical assembly in accordance with approved drawings.

Check:

- correct enclosure used

- mounting plate installed correctly

- gland plates installed correctly

- door furniture fitted correctly

- components mounted as drawing

- trunking and DIN rail installed correctly

- ventilation / fans / heaters fitted where required

- earthing points provided

- access and maintenance space maintained

- build is clean and professional

Mechanical assembly must be inspected and signed off before progressing to wiring.

6. Pre-Build Review

Gate 4 – Build Released

Complete a pre-build review before physical manufacture starts.

Confirm:

- latest approved drawings are available

- BOM is complete

- major components are available

- enclosure type and rating are correct

- workshop resource is available

- build sequence is understood

- inspection points are identified

- FAT / testing requirements are understood

- client witness points are identified where required

No build shall commence until the pre-build review confirms that manufacture can proceed safely and correctly.

Supporting Documents:

5. Procurement & Material Control

Gate 3 – Materials Checked

Procure materials and components in accordance with the approved design and bill of materials.

Check:

- components match approved design

- ratings are correct

- delivery dates support programme

- damaged / incorrect items are quarantined

- substitutions are technically approved before use

- long lead items are monitored

No component substitution shall be made without technical approval.

4. Design Review & Approval for Manufacture

Gate 2 – Design Approved for Manufacture

Review and approve the design before manufacture starts.

Confirm:

- design matches customer requirements

- components are suitable

- ratings are suitable

- drawings are complete

- cable sizing and protective devices are suitable

- labelling is clear

- access and maintenance requirements are considered

- testing requirements are defined

- any customer approval has been received where required

No manufacture shall start until the design has been approved for manufacture.

3. Design Development

Pre-Gate Activity for Gate 2

Develop the design information required for manufacture.

Prepare, where applicable:

- general arrangement drawings

- panel layout drawings

- door layout drawings

- electrical schematics

- single line diagrams

- cable schedules

- terminal schedules

- I/O schedules

- bill of materials

- PLC / HMI requirements

- control philosophy / description of operation

- labelling schedule

Design information shall be developed, checked and controlled by revision before being submitted for approval to manufacture.

2. Technical Clarification / RFI Review

Linked to Gate 1 – Order / Design Input Review Complete

Review whether any information is missing, unclear or conflicting.

Check:

- control philosophy

- process requirements

- incoming supply details

- environmental requirements

- IP rating

- form of separation where applicable

- short circuit / fault level where applicable

- cable entry requirements

- client standards

- emergency stop and safety requirements

- interfaces with other systems

Raise RFIs / technical queries where information is incomplete or unclear.

- 02-05-19-11 – Manufacturing Handover Pack Checklist

- Handover Pack Checklist

- 02-05-19-16 – Verification Record

- 02-05-19-17/18 – Declaration of Conformity

11. Documentation & Handover Pack

Gate 9 – Documentation and Handover Pack Complete

Collate and check the final documentation before release.

Documentation may include:

- as-built drawings

- electrical schematics

- general arrangement drawings

- bill of materials

- test certificates

- FAT record

- routine verification record

- declaration of conformity / incorporation where applicable

- technical file information where applicable

- PLC / HMI backup

- O&M information

- component manuals

- warranty information

- recommended spares list where applicable

- snag close-out record

Documentation must reflect the final manufactured equipment.

- 02-05-19-11 – Manufacturing Handover Pack Checklist

- 02-05-19-07 – Flash Test Record

- 02-05-19-19 – Torque Record Checklist

- 02-04-20 – Purchasing Sheet

- 02-04-21 – Supplier Quotation Request

- 02-05-01-18 – Procurement Tracker

- 02-05-19-15 – Steelwork inspection checklist

- 02-05-19-03 – LV Assembly Design Review & Sign-Off

12. Packing, Dispatch & Delivery

Gate 10 – Dispatch Approved

Check, protect and prepare the equipment for dispatch.

Confirm:

- equipment cleaned

- loose items removed or secured

- keys and accessories packed and labelled

- documentation issued or packed

- doors secured

- components protected

- transport protection applied

- delivery address confirmed

- delivery date confirmed

- photos taken where required

- dispatch approved by responsible person

No equipment shall be dispatched until all required inspections, tests, documents and approvals are complete or formally accepted.

- 02-05-19-10 – Packing, Dispatch & Delivery Checklist

- 02-05-19-11 – Manufacturing Handover Pack Checklist

- 02-05-01-05 – Drawing Register

- 02-05-01-11 – Technical Submission Register

- 02-05-01-12 – Technical Submission

- 02-05-19-20 - Design Risk Assessment

- 02-05-19-13 – Bill of Materials

- 02-05-19-09 – Manufacturing Snag / Non-Conformance Register

- 02-05-19-12 – Manufacturing Register

14. Manufacturing Close-Out & Review

Final Close-Out – Manufacturing Job Closed

Close the manufacturing job once all records are complete.

Confirm:

- equipment completed

- inspection and testing complete

- FAT complete where required

- snags closed or formally accepted

- documentation issued

- delivery records saved

- manufacturing register updated

- lessons learned recorded where required

A post-manufacture review should be completed for significant projects, repeat defects, complaints, programme delays, first-of-type panels or high-value equipment.

This is a close-out activity and does not replace Gate 10 dispatch approval.

13. Installation / Commissioning Interface

Post-Dispatch Interface

Where COMPANY NAME is installing or commissioning the equipment, the relevant project, site or commissioning team must receive the required information.

- Provide:

- as-built drawings

- cable entry details

- lifting / handling requirements

- installation limitations

- commissioning requirements software / programming requirements

- residual risks

- open actions agreed for site completion

This stage does not create a new gate. It supports site installation, commissioning and handover after dispatch approval.

- 02-05-19-08 – Functional Test & FAT Record

- 02-05-19-09 – Manufacturing Snag / Non-Conformance Register

- 02-05-19-07 – Routine Verification / Electrical Test Record

9. Routine Verification / Electrical Testing

Gate 7 – Electrical Testing Complete

Complete electrical inspection and testing before functional testing or dispatch.

Testing may include:

- visual inspection

- protective bonding continuity

- insulation resistance

- polarity checks

- point-to-point wiring checks

- control circuit checks

- protective device checks

- door interlock checks where applicable

- emergency stop checks where applicable

- verification of warning labels, shrouds and barriers

Test equipment must be suitable and calibrated where required.

10. Functional Testing / FAT

Gate 8 – Functional Test / FAT Complete

Complete functional testing and Factory Acceptance Testing where required.

Testing may include:

- power-up checks where safe and applicable

- control circuit operation

- functional sequence testing

- alarm and trip testing

- PLC / HMI checks

- input / output simulation

- manual / auto controls

- local / remote operation

- safety interlocks

- customer witness testing where required

Snags identified during FAT must be recorded and closed out before dispatch unless formally accepted.

8. Wiring & Internal Assembly

Gate 6 – Wiring Inspection Complete

Complete wiring and internal assembly in accordance with approved schematics and schedules.

Check:

- correct cable type, size and colour

- ferrules fitted

- terminal references correct

- power / control / ELV / communication segregation maintained

- screened cables terminated correctly

- protective bonding complete

- terminals tightened

- torque settings applied where required

- labels fitted

- no loose strands or exposed conductors

- workmanship is neat and professional

Wiring shall be checked and signed off before electrical testing.

- 02-05-19-06 – Wiring & Internal Assembly Inspection Checklist

- 02-05-19-05 – Manufacturing Build Checklist

- 02-05-19-01 – Manufacturing Job Pack / Index Sheet

- 02-05-19-05 – Manufacturing Build Checklist

- 02-05-19-01 – Manufacturing Job Pack / Index Sheet

- 02-05-19-02 – Design Input Review Checklist

- 02-05-19-04 – LV Assembly Specification Form

- 02-01-07 – RFI Template

- 02-01-08 – RFI / TQ Register