## Recovery-hr
Project No.
Project
Title
Schedule No.
Revision
Date
Capacity HW used in each appliance |  |  |  | 1 |  | (or 0.66)
No hours recovery |  |  |  | 1 | hrs.
CW Temperature rise |  |  |  | 50 | °C
Sanitaryware |  | Capacity |  | Total HW per use
WHBs |  | 5 | litres | 5 | litres
Cleaners Sinks |  | 12 | litres | 12 | litres (tend to be un-blended)
Sinks |  | 12 | litres | 12 | litres
Kitchen Sinks |  | 12 | litres | 12 | litres (tend to be un-blended)
Shower |  | 40 | litres | 40 | litres
Bath |  | 100 | litres | 100 | litres
Peak Usage Volume Check - lunchtime
Sanitaryware |  | QTY |  | No. Uses Per Hour |  | Total HW per Hr.
WHBs |  | 19 | no. | 3 | no. | 285 | litres
Sinks |  | 4 | no. | 3 | no. | 144 | litres
Kitchen Sink (Staff?) |  | 2 | no. | 0 | no. | 0 | litres
Bath |  | 0 | no. | 0 | no. | 0 | litres
Shower |  | 4 | no. | 0.5 | no. | 80 | litres
509
HW Usage / Recovery Rate
Total | 509 |  |  | litres/hr
Heat Input | 15000 | x | 4.2 | x | 50 | = | 875 | kW
3600
[7 empty] | 1006.25 | 15% Margin
Options
kW
[7 empty] | 0% | Duty/Load
[7 empty] | 0% | Duty/Load
kW
[7 empty] | 0% | Duty/Load
[7 empty] | 0% | Duty/Load
kW
[7 empty] | 0% | Duty/Load
[7 empty] | 0% | Duty/Load
IP 02-05-13-5303 Version 1