## 4.0 Index Resistances (SF1&EF5) (hidden)
4.0 Index Resistances (CIP)
|  | SUPPLY FAN | [11 empty] | K FACTORS FOR SECTIONS
| Sec. | Volume | Duct | Duct | Duct | Length | P.D. | VEL | Vel. P. | K. Fac | Resistance Pa |  |  | Bends |  |  | Tees |  |  | Other |  |  |  | Total in
| No. | m3/s | Size | H | W | m | Pa/m | m/s | Pa |  | Straight | Fittings | Total | No | k | Tot | No | k | Tot |  | No | k | Tot | Sect.
| PRIMARY | [22 empty] | 0
| Bell Mouth | 1.578 | [21 empty] | 0
| 1 | 1.578 | 560 |  |  | 6 | 0.76 | 6.41 | 24.6529 | 1.25 | 4.56 | 30.8161 | 35.3761 | 2 | 0.55 | 1.1 |  |  |  | BELLMOUTH | 1 | 0.15 | 0.15 | 1.25
| Cowl | [10 empty] | 25 | 60.3761 | [10 empty] | 0
[10 empty] | TOTAL (+20% margin) |  | 72.4513
|  | EXTRACT FAN | [11 empty] | K FACTORS FOR SECTIONS
| Sec. | Volume | Duct | Duct | Duct | Length | P.D. | VEL | Vel. P. | K. Fac | Resistance Pa |  |  | Bends |  |  | Tees |  |  | Other |  |  |  | Total in
| No. | m3/s | Size | H | W | m | Pa/m | m/s | Pa |  | Straight | Fittings | Total | No | k | Tot | No | k | Tot |  | No | k | Tot | Sect.
| PRIMARY | [22 empty] | 0
0
| Cowl | [10 empty] | 10 | 10 | [10 empty] | 0
[10 empty] | TOTAL (+20% margin) |  | 12
|  | 1.578 |  | l/s | 72.4513 |  | pa | Supply
|  | 1.578 |  | l/s | 12 |  | pa | Extract

## 4.0 Index Resistances (HRU)
Key Integrated Services Ltd Unit 2, Bollin Court, Mill Lane, Lymm, Cheshire, WA13 9SX TEL: 01925 759948 FAX: 01925 758400
Project No.
Project
Title
Schedule No.
Revision
Date
Sheet
4.0 Index Resistances
AHU 01
SUPPLY FAN | [12 empty] | K FACTORS FOR SECTIONS
Sec. | Volume | Duct | Duct | Duct | Length | P.D. | VEL | Vel. P. | K. Fac | Resistance Pa | Fittings | Total | Bends |  |  | Tees |  |  | Other |  |  |  | Total in
No. | m3/s | Size | H | W | m | Pa/m | m/s | Pa |  | Straight | Pa | Pa | No | k | Tot | No | k | Tot |  | No | k | Tot | Sect.
PRIMARY
Diff | [10 empty] | Pa: 0 |  |  |  |  | 0
[11 empty] | Pa: 0 |  |  |  |  | 0
[11 empty] | Pa: 0 |  |  |  |  | 0
[11 empty] | Pa: 0 |  |  |  |  | 0
[11 empty] | Pa: 0 |  |  |  |  | 0
Louvre | [10 empty] | Pa: 0
Attenuator | [10 empty] | Pa: 0
0
[9 empty] | TOTAL (+10% margin) |  | Pa: 0
AHU 01 |  |  |  | l/s | 0 |  | pa | Supply
AHU 01
Extract FAN | [10 empty] | No: K FACTORS FOR SECTIONS
Sec. | Volume | Duct | Duct | Duct | Length | P.D. | VEL | Vel. P. | K. Fac | Resistance Pa | Pa: Fittings; Pa: Total; No: Bends; No: Tees | Other |  |  |  | Total in
No. | m3/s | Size | H | W | m | Pa/m | m/s | Pa |  | Straight | Pa | Pa | No | k | Tot | No | k | Tot |  | No | k | Tot | Sect.
[11 empty] | Pa: 0 |  |  |  |  | 0
[11 empty] | Pa: 0 |  |  |  |  | 0
0
0
[11 empty] | Pa: 0 |  |  |  |  | 0
0
0
0
[9 empty] | TOTAL (+10% margin) |  | Pa: 0
AHU 01 |  |  |  | l/s | 0 |  | pa | Extract
IP 02-05-13-5703 Version 1
2.0 Sizing Criteria
Design Information Required
1. Ductwork index run pressure drop (Pa)
2. Damper pressure drops (Pa)
3. Louvre/mesh pressure drops (Pa)
4. Total system flow rate (m³/s)
Step 1
Calculate the ductwork index run pressure drop including for fittings, dampers, louvres etc.
Step 2
Calculate the systems total volume flow rate
Step 3
Select an appropriate fan that appears to operate within the calculated parameters ensuring compliance with specific fan powers (w/l/s) using selected manufacturers data.
Sec. | Volume | Duct | Duct | Duct | Length | P.D. | VEL | Vel. P. | K. Fac | Resistance Pa | No: Bends; No: Tees | Other |  |  |  | Total in
No. | m3/s | Size | H | W | m | Pa/m | m/s | Pa |  | Straight | Fittings | Total | No | k | Tot | No | k | Tot |  | No | k | Tot | Sect.
PRIMARY
Diff | [10 empty] | Pa: 25; Pa: 25 |  |  |  |  | 0
1 | 0.05 | 150 |  |  | 6 | 0.84 | 2.7 | 4.374 | 0.75 | 5.04 | 3.2805 | 33.3205 | 1 | 0.55 | 0.55 |  |  |  | VCD | 1 | 0.2 | 0.2 | 0.75
2 | 0.09 | 200 |  |  | 3 | 0.6 | 2.86 | 4.9078 | 0.6 | 1.8 | 2.9447 | 38.0652 |  |  |  | 2 | 0.3 | 0.6 |  |  |  |  | 0.6
Transition | 0.095 | 200 |  |  | 0.5 | 0.66 | 3.02 | 5.4722 | 0.65 | 0.33 | 3.557 | 41.9521 |  |  |  | 2 | 0.3 | 0.6 | Transition | 1 | 0.05 | 0.05 | 0.65
3 | 0.28 | 315 |  |  | 3 | 0.52 | 3.59 | 7.7329 | 1.4 | 1.56 | 10.826 | 54.3381 | 2 | 0.55 | 1.1 | 1 | 0.3 | 0.3 |  |  |  |  | 1.4
HB | [10 empty] | Pa: 25; Pa: 79.3381 |  |  |  |  | 0
[9 empty] | TOTAL (+21.1% margin) |  | Pa: 95.9991
#REF! |  | 0.308 |  | l/s | 95.9991 |  | pa | Supply
SUPPLY FAN | [10 empty] | No: K FACTORS FOR SECTIONS
Sec. | Volume | Duct | Duct | Duct | Length | P.D. | VEL | Vel. P. | K. Fac | Resistance Pa | No: Bends; No: Tees | Other |  |  |  | Total in
No. | m3/s | Size | H | W | m | Pa/m | m/s | Pa |  | Straight | Fittings | Total | No | k | Tot | No | k | Tot |  | No | k | Tot | Sect.
PRIMARY
Diff | [10 empty] | Pa: 25; Pa: 25 |  |  |  |  | 0
1 | 0.051 | 150 |  |  | 9 | 0.87 | 2.89 | 5.0113 | 1.3 | 7.83 | 6.5146 | 39.3446 | 2 | 0.55 | 1.1 |  |  |  | VCD | 1 | 0.2 | 0.2 | 1.3
Transition | 0.099 | 200 |  |  | 0.5 | 0.71 | 3.15 | 5.9535 | 0.05 | 0.355 | Pa: 0.29767; Pa: 39.9973 | Transition | 1 | 0.05 | 0.05 | 0.05
2 | 0.099 | 200 |  |  | 12 | 0.71 | 3.15 | 5.9535 | 0.6 | 8.52 | 3.5721 | 52.0894 |  |  |  | 2 | 0.3 | 0.6 |  |  |  |  | 0.6
3 | 0.29 | 250 |  |  | 12 | 0.94 | 4.26 | 10.8886 | 0.6 | 11.28 | 6.5331 | 69.9025 |  |  |  | 2 | 0.3 | 0.6 |  |  |  |  | 0.6
Transition | 0.14 | 250 |  |  | 0.5 | 0.45 | 2.85 | 4.8735 | 0.05 | 0.225 | Pa: 0.24368; Pa: 70.3712 | Transition | 1 | 0.05 | 0.05 | 0.05
4 | 0.269 | 315 |  |  | 12 | 0.48 | 3.45 | 7.1415 | 1.15 | 5.76 | 8.2127 | 84.3439 | 1 | 0.55 | 0.55 | 2 | 0.3 | 0.6 |  |  |  |  | 1.15
HB | [10 empty] | Pa: 25; Pa: 109.3439 |  |  |  |  | 0
[9 empty] | TOTAL (+21.1% margin) |  | Pa: 132.3062
#REF! |  | 0.319 |  | l/s | 132.3062 |  | pa | Supply
SUPPLY FAN | [10 empty] | No: K FACTORS FOR SECTIONS
Sec. | Volume | Duct | Duct | Duct | Length | P.D. | VEL | Vel. P. | K. Fac | Resistance Pa | No: Bends; No: Tees | Other |  |  |  | Total in
No. | m3/s | Size | H | W | m | Pa/m | m/s | Pa |  | Straight | Fittings | Total | No | k | Tot | No | k | Tot |  | No | k | Tot | Sect.
PRIMARY
Diff | [10 empty] | Pa: 25; Pa: 25 |  |  |  |  | 0
1 | 0.025 | 125 |  |  | 3 | 0.58 | 2.04 | 2.497 | 1.6 | 1.74 | 3.9951 | 30.7351 | 2 | 0.55 | 1.1 | 1 | 0.3 | 0.3 | VCD | 1 | 0.2 | 0.2 | 1.6
2 | 0.05 | 150 |  |  | 9 | 0.84 | 2.7 | 4.374 | 1.15 | 7.56 | 5.0301 | 43.3252 | 1 | 0.55 | 0.55 | 2 | 0.3 | 0.6 |  |  |  |  | 1.15
Transition | 0.1 | 200 |  |  | 0.5 | 0.73 | 3.18 | 6.0674 | 0.05 | 0.365 | Pa: 0.30337; Pa: 43.9936 | Transition | 1 | 0.05 | 0.05 | 0.05
3 | 0.1 | 200 |  |  | 3 | 0.73 | 3.18 | 6.0674 | 1.7 | 2.19 | 10.3146 | 56.4983 | 2 | 0.55 | 1.1 | 2 | 0.3 | 0.6 |  |  |  |  | 1.7
HB | [10 empty] | Pa: 25; Pa: 81.4983 |  |  |  |  | 0
[9 empty] | TOTAL (+21.1% margin) |  | Pa: 98.6129
#REF! |  | 0.11 |  | l/s | 98.6129 |  | pa | Supply
EXTRACT FAN | [10 empty] | No: K FACTORS FOR SECTIONS
Sec. | Volume | Duct | Duct | Duct | Length | P.D. | VEL | Vel. P. | K. Fac | Resistance Pa | No: Bends; No: Tees | Other |  |  |  | Total in
No. | m3/s | Size | H | W | m | Pa/m | m/s | Pa |  | Straight | Fittings | Total | No | k | Tot | No | k | Tot |  | No | k | Tot | Sect.
PRIMARY
Diff | [10 empty] | Pa: 25; Pa: 25 |  |  |  |  | 0
1 | 0.052 | 150 |  |  | 6 | 0.9 | 3 | 5.4 | 1.05 | 5.4 | 5.67 | 36.07 | 1 | 0.55 | 0.55 | 1 | 0.3 | 0.3 | VCD | 1 | 0.2 | 0.2 | 1.05
Transition | 0.104 | 200 |  |  | 0.5 | 0.78 | 3.31 | 6.5737 | 0.05 | 0.39 | Pa: 0.32868; Pa: 36.7887 | Transition | 1 | 0.05 | 0.05 | 0.05
2 | 0.099 | 200 |  |  | 6 | 0.71 | 3.15 | 5.9535 | 0.3 | 4.26 | 1.786 | 42.8347 |  |  |  | 1 | 0.3 | 0.3 |  |  |  |  | 0.3
3 | 0.208 | 250 |  |  | 12 | 0.94 | 4.24 | 10.7866 | 2.5 | 11.28 | 26.9664 | 81.0811 | 4 | 0.55 | 2.2 | 1 | 0.3 | 0.3 |  |  |  |  | 2.5
4 | 0.336 | 315 |  |  | 12 | 0.73 | 4.31 | 11.1457 | 2.5 | 8.76 | 27.8641 | 117.7053 | 4 | 0.55 | 2.2 | 1 | 0.3 | 0.3 |  |  |  |  | 2.5
[9 empty] | TOTAL (+21.1% margin) |  | Pa: 142.4234
#REF! |  | 0.3696 |  | l/s | 142.4234 |  | pa | Extract
EXTRACT FAN | [10 empty] | No: K FACTORS FOR SECTIONS
Sec. | Volume | Duct | Duct | Duct | Length | P.D. | VEL | Vel. P. | K. Fac | Resistance Pa | No: Bends; No: Tees | Other |  |  |  | Total in
No. | m3/s | Size | H | W | m | Pa/m | m/s | Pa |  | Straight | Fittings | Total | No | k | Tot | No | k | Tot |  | No | k | Tot | Sect.
PRIMARY
Diff | [10 empty] | Pa: 30; Pa: 30 |  |  |  |  | 0
1 | 11.4 |  | 1000 | 1000 | 20 | 1.1 | 6 | 21.6 | 0.2 | 22 | Pa: 4.32; Pa: 56.32 | VCD | 1 | 0.2 | 0.2 | 0.2
2 | 23.4 | 200 | 2000 | 1000 | 20 | 0.81 | 9 | 48.6 | 0 | 16.2 | Pa: 0; Pa: 72.52 |  |  |  |  | 0
3 | 29.25 | 200 | 2200 | 1500 | 65 | 0.31 | 9 | 48.6 | 5.7 | 20.15 | 277.02 | 369.69 | 10 | 0.55 | 5.5 |  |  |  | VCD | 1 | 0.2 | 0.2 | 5.7
369.69
369.69
[9 empty] | TOTAL (+21.1% margin) |  | Pa: 447.3249
797.3249
#REF! |  | 32.175 |  | l/s | 447.3249 |  | pa | Extract